## Duct Flow
Duct loss due to wall friction (circular duct, air at 20 C)
(Ref: FDS Technical Reference Guide, NIST Special Publication 1018)
Input
| Dia = | 0.3048 | m
| Flow = | 1 | m^3/s
| Roughness (ε)= | 0.001 | m
| Length = | 1 | m
| Vent Area = | 0.16 | m^2
| Kinematic Visc = | 1.511e-05 | m^2/s
| Re = | 276458.9738
| Density = | 1.205 | kg/m^3
| Duct Area = | 0.072966 | m^2
| Duct Vel = | 13.705 | m/s
| RHS = | 6.0522
| f = | 0.027301
Calculated Flow Parameters
| K = | 0.089569
| Pressure Loss = | 10.1362 | Pa
| Vent Velocity = | 6.25 | m/s
| Mass Flow Rate = | 1.205 | kg/s
This software is provided as is, and no claim is made as to the accuracy or suitability of this software. The user takes full and exclusive responsibility for using this software.
Please report any errors to: support@thunderheadeng.com