{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Input","Data","Output"],"not_rendered":{"charts":1,"images":2,"macros":1,"external_links":0,"defined_names":13,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Input","index":0,"n_rows":21,"n_cols":7,"rows_kept":21,"cut":false,"hidden":false,"merged":[[12,1,12,2],[18,1,18,6],[12,3,12,6],[11,1,11,6]]}
[]
["Calculates HRR for different fires using a t2 fire for growth and decay periods, with a constant max between these two periods."]
[null,"Ref: Heat Release Rates of Burning Items in Fires, Hyeong-Jin Kim and David G. Lilley, AIAA 2000-0722, 38th Aerospace Sciences Meeting & Exhibit, 10-13 January 2000, Reno, NV."]
{"$rows_empty":8}
[null,"Select fire type"]
[null,"Fire Type: ",null,"Wardrobe 1 - FASTLite"]
[null,null,"Divisions in Graph:",200]
[]
[]
[]
[]
[null,"Parameters in Calculations (Do not edit)"]
[null,"t0","tl0","td","tend","αg","αd"]
[null,0,60,90,500,0.81632700000000002,1.7482000000000001E-2]

{"sheet":"Data","index":1,"n_rows":67,"n_cols":12,"rows_kept":67,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Name","Description","t0","t1 MW","tl0","td","tend","Q-dotmax","tg","αg","αd"]
[null,"Wardrobe 1 - FASTLite","1/2\" Plywood wardrobe,  clothing on 16 hangers ",0,35,60,90,500,2938.8,35,0.81632700000000002,1.7482000000000001E-2]
[null,"Wardrobe 2 - FASTLite","1/8\" Plywood wardrobe,  clothing on 16 hangers ",0,40,100,110,140,6250,40,0.625,6.9444439999999998]
[null,"Wardrobe 3 - FASTLite","1/8\" Plywood wardrobe,  FR paint, clothing on 16 hangers ",0,30,70,80,400,5444.4,30,1.111111,5.3168E-2]
[null,"Wardrobe 4 - FASTLite","1/8\" Plywood wardrobe,  FR paint, clothing on 16 hangers ",0,90,150,160,450,2777.8,90,0.123457,3.3029000000000003E-2]
[null,"Wardrobe 5 - FASTLite","3/4\" Particle-board wardrobe,  thin plastic coating ",0,150,170,670,2000,1284.4000000000001,150,4.4443999999999997E-2,7.2599999999999997E-4]
[null,"Chair 1 - FASTLite","Chair, one-piece wood-reinforced urethane foam",0,1000,650,660,1900,422.5,1000,1E-3,2.7500000000000002E-4]
[null,"Chair 2 - FASTLite","Chair, polypropylene foam frame, urethane foam, polyolefin fabric",0,100,140,160,500,1960,100,0.1,1.6955000000000001E-2]
[null,"Chair 3 - FASTLite","Chair, thin wood frame, California foam, polyolefin fabric",0,200,175,176,900,765.6,200,2.5000000000000001E-2,1.4610000000000001E-3]
[null,"Chair 4 - FASTLite","Chair, urethane foam frame, urethane foam, polyolefin fabric",0,60,60,210,430,1000,60,0.27777800000000002,2.0660999999999999E-2]
[null,"Chair 5 - FASTLite","Chair, wood frame, California foam, Haitian cotton fabric",0,350,275,475,1000,617.29999999999995,350,8.1630000000000001E-3,2.2399999999999998E-3]
[null,"Chair 6 - FASTLite","Chair, wood frame, California foam, polyolefin fabric",0,50,70,90,315,1960,50,0.4,3.8716E-2]
[null,"Chair 7 - FASTLite","Chair, wood frame, FR cotton stuffing, Haitian cotton fabric",0,2000,210,310,1000,11,2000,2.5000000000000001E-4,2.3E-5]
[null,"Chair 8 - FASTLite","Chair, wood frame, FR cotton stuffing, polyolefin fabric",0,400,275,475,1000,472.7,400,6.2500000000000003E-3,1.7149999999999999E-3]
[null,"Chair 9 - FASTLite","Chair, wood frame, urethane foam, cotton fabric",0,200,90,310,550,202.5,200,2.5000000000000001E-2,3.516E-3]
[null,"Chair 10 - FASTLite","Chair, wood frame, urethane foam, cotton fabric",0,75,50,250,1250,444.4,75,0.17777799999999999,4.44E-4]
[null,"Chair 11 - FASTLite","Chair, wood frame, urethane foam, cotton fabric, polyester batting",0,425,347,367,1000,666.6,425,5.5360000000000001E-3,1.6639999999999999E-3]
[null,"Chair 12 - FASTLite","Chair, wood frame, urethane foam, polyolefin fabric",0,80,160,170,420,4000,80,0.15625,6.4000000000000001E-2]
[null,"Chair 13 - FASTLite","Chair, wood frame, urethane foam, quilted cotton/plyolefin, polyester batting",0,200,187,200,500,874.2,200,2.5000000000000001E-2,9.7140000000000004E-3]
[null,"Bed - FASTLite Data","Innerspring mattress and boxspring, cotton felt/urethane/sisal cover",0,1100,680,1080,1300,382.1,1100,8.2600000000000002E-4,7.8960000000000002E-3]
[null,"Lounge chair 1 - FASTLite Data","Lounge chair, metal frame, urethane foam, plastic-coated fabric",0,350,170,220,350,235.9,350,8.1630000000000001E-3,1.396E-2]
[null,"Lounge chair 2 - FASTLite Data","Lounge chair, one-piece molded glass fiber, metal legs",0,120,20,21,150,27.8,120,6.9444000000000006E-2,1.6689999999999999E-3]
[null,"Lounge chair 3 - FASTLite Data","Lounge chair, one-piece molded thermoplastic",0,275,230,430,900,699.5,275,1.3223E-2,3.1670000000000001E-3]
[null,"Lounge chair 4 - FASTLite Data","Lounge chair, wood frame, latex foam/cotton stuffing, plastic-coated fabric ",0,500,130,140,300,67.599999999999994,500,4.0000000000000001E-3,2.6410000000000001E-3]
[null,"Loveseat 1 - FASTLite Data","Loveseat, mixed foam and cotton batting stuffing, cotton fabric ",0,400,350,400,2000,765.6,400,6.2500000000000003E-3,2.99E-4]
[null,"Loveseat 2 - FASTLite Data","Loveseat, wood frame, California foam, polyolefin fabric ",0,80,130,160,400,2640.6,80,0.15625,4.5844000000000003E-2]
[null,"Loveseat 3 - FASTLite Data","Loveseat, wood frame, urethane foam, plastic-coated fabric ",0,350,330,430,1500,889,350,8.1630000000000001E-3,7.76E-4]
[null,"Metal wardrobe 1 - FASTLite Data","Metal wardrobe, clothing on 16 hangers ",0,250,125,150,500,250,250,1.6E-2,2.0409999999999998E-3]
[null,"Metal wardrobe 2 - FASTLite Data","Metal wardrobe, clothing on 8 hangers ",0,50,40,47,200,640,50,0.4,2.734E-2]
[null,"Patient lounge chair - FASTLite Data","Patient lounge chair, metal frame, urethane foam cushion ",0,170,80,90,150,221.5,170,3.4602000000000001E-2,6.1515E-2]
[null,"Sofa 1 - FASTLite Data","Sofa, metal frame, urethane foam, plastic-coated fabric ",0,500,260,460,800,270.39999999999998,500,4.0000000000000001E-3,2.3389999999999999E-3]
[null,"Sofa 2 - FASTLite Data","Sofa, wood frame, California foam, polyolefin fabric ",0,100,170,250,430,2890,100,0.1,8.9198E-2]
[null,"F21 Chair - FASTLite Data","F21 Chair, wood frame, polyurethane foam, olefin fabric ",140,215,250,250,360,2151.1,75,0.17777799999999999,0.17777799999999999]
[null,"F31 Loveseat - FASTLite Data","F31 Loveseat, wood frame, polyurethane foam, olefin fabric ",90,165,215,265,390,2777.8,75,0.17777799999999999,0.17777799999999999]
[null,"F32 Sofa - FASTLite Data","F32 Sofa, wood frame, polyurethane foam, olefin fabric ",75,150,205,270,400,3004.4,75,0.17777799999999999,0.17777799999999999]
[null,"Bed 1 - HAZARD Data","Double bed, bedding, night table, gypsum bd walls",169,211,230,230,936,2109.4,42,0.56689299999999998,4.2319999999999997E-3]
[null,"Bed 2 - HAZARD Data","Double bed, bedding, night table, plywood walls",164,239,360,430,998,6829.5,75,0.17777799999999999,2.1169E-2]
[null,"Chair 1 (F21) - HAZARD Data","Upholstered chair,F21 , wood frame, pu foam-fr, olefin ",126,218,260,260,607,2121.5,92,0.118147,1.7618999999999999E-2]
[null,"Chair 2 (F23) - HAZARD Data","Chair, F23,wood frame, fr cotton batting,olefin ",0,538,450,450,1932,699.6,538,3.4550000000000002E-3,3.19E-4]
[null,"Chair 3 (F25) - HAZARD Data","Upholstered chair, F25, wood frame, pu foam, olefin",106,215,260,260,679,1996.1,109,8.4168000000000007E-2,1.137E-2]
[null,"Chair 4 (F28) - HAZARD Data","Upholstered chair, F28, wood frame, pu/pe/ctn bedding, cotton",82,478,420,420,1184,728.5,396,6.3769999999999999E-3,1.248E-3]
[null,"Chair 5 (F30) - HAZARD Data","Upholstered chair, F30, pu frame, pu foam, olefin",40,140,130,263,1017,810,100,0.1,1.4250000000000001E-3]
[null,"Chair 6 - HAZARD Data","Bean bag chair, vinyl/ps foam beads",88,748,545,718,1228,479.5,660,2.2959999999999999E-3,1.843E-3]
[null,"Chair 7 - HAZARD Data","Char, molded flexible pu frame, pu cover ",644,1662,1330,1330,2685,454.1,1018,9.6500000000000004E-4,2.4699999999999999E-4]
[null,"Chair 8 - HAZARD Data","Easy chair, molded ps foam frame,pu pad and cover ",38,245,240,240,883,952.3,207,2.3338000000000001E-2,2.3029999999999999E-3]
[null,"Christmas Tree - HAZARD Data","Christmas tree, spruce, dry ",290,327,320,350,478,657.4,37,0.73046,4.0125000000000001E-2]
[null,"Cooking Oil - HAZARD Data","Cooking, Corn, Cottonseed, Etc in 12inch pan ",0,15,5,1000,1000,111.1,15,4.4444439999999998]
[null,"Curtain - HAZARD Data","Curtain, Cotton, 0.31 kg/m2",123,229,175,175,411,240.7,106,8.8999999999999996E-2,4.3210000000000002E-3]
[null,"Loveseat (F31) - HAZARD Data","Loveseat, F31, wood frame, pu foam(fr), olefin ",71,165,229,249,701,2825.3,94,0.113173,1.3828999999999999E-2]
[null,"Mattress 1 - HAZARD Data","Mattress, m05, wood frame, pu foam, rayon ticking, bedding ",269,437,480,480,933,1577.4,168,3.5430999999999997E-2,7.6870000000000003E-3]
[null,"Mattress 2 - HAZARD Data","Mattress and boxspring (westchase hilton) ",144,858,606,980,2233,418.7,714,1.9620000000000002E-3,2.6699999999999998E-4]
[null,"Sofa (F32) - HAZARD Data","Upholstered/sofa, F32, wood\\frame, pu foam-fr,olefin",74,154,211,283,651,2932.7,80,0.15625,2.1655000000000001E-2]
[null,"Trash Bags - HAZARD Data","Trash bags (3), paper ",0,100,58,111,517,336.4,100,0.1,2.0409999999999998E-3]
[null,"TV Set - HAZARD Data","Television set, b/w, wood cabinet ",304,984,670,670,1872,289.7,680,2.163E-3,2.0100000000000001E-4]
[null,"Wardrobe - HAZARD Data","Wardrobe closet, plywood, fr paint ",70,113,170,170,358,5408.3,43,0.54083300000000001,0.15301999999999999]
[null,"Waste Basket - HAZARD Data","Wastepaper baskete, polythylene, milk cartons ",115,2034,350,350,1264,15,1919,2.72E-4,1.8E-5]
[null,"Bunk Bed - BFRL Data","BFRL in February 1996. ",186,211,240,240,445,4665.6000000000004,25,1.6,0.11101999999999999]
[null,"Koisk - BFRL Data","Western Fire Center in the summer of 1995 ",817,1129,1230,1230,3300,1752.2,312,1.0272999999999999E-2,4.0900000000000002E-4]
[null,"Loveseat - BFRL Data",null,48,222,350,371,866,3012.4,174,3.3029000000000003E-2,1.2293999999999999E-2]
[null,"Mattress (Center) - BFRL Data","BFRL in February 1996. ",9,173,145,219,959,687.7,164,3.7179999999999998E-2,1.256E-3]
[null,"Mattress (Corner) - BFRL Data","BFRL in February 1996. ",85,294,295,321,484,1009.6,209,2.2893E-2,3.7998999999999998E-2]
[null,"Small Dresser - BFRL Data","BFRL in February 1996 ",112,346,423,423,870,1766.4,234,1.8263000000000001E-2,8.8400000000000006E-3]
[null,"Sofa - BFRL Data",null,26,222,390,399,931,3449,196,2.6030999999999999E-2,1.2186000000000001E-2]
[null,"Wooden Pallet - BFRL Data","BFRL in February 1996. ",0,467,634,664,1616,1843.1,467,4.5849999999999997E-3,2.0339999999999998E-3]
[null,"Workstation (2 panels) - BFRL Data","Sponsored by GSA and performed at BFRL in 1991 ",132,244,280,280,3276,1746.2,112,7.9718999999999998E-2,1.95E-4]
[null,"Workstation (3 panels) - BFRL Data","Sponsored by GSA and performed at BFRL in 1991.  ",283,386,550,550,1142,6719.7,103,9.4259999999999997E-2,1.9174E-2]

{"sheet":"Output","index":2,"n_rows":204,"n_cols":3,"rows_kept":204,"cut":false,"hidden":false,"merged":[]}
[null,"HRR Max (kW) =",2938.7772]
[null,"Total Heat Release (MJ) =",548.62305362500001]
["Time (s)","Normalized","HRR (kW)"]
[0,0,0]
[2.5,1.736111111111111E-3,5.10204375]
[5,6.9444444444444441E-3,20.408175]
[7.5,1.5625E-2,45.91839375]
[10,2.7777777777777776E-2,81.6327]
[12.5,4.3402777777777783E-2,127.55109375000001]
[15,6.25E-2,183.673575]
[17.5,8.5069444444444448E-2,250.00014375000001]
[20,0.1111111111111111,326.5308]
[22.5,0.140625,413.26554375000001]
[25,0.17361111111111113,510.20437500000003]
[27.5,0.21006944444444448,617.34729375000006]
[30,0.25,734.6943]
[32.5,0.29340277777777779,862.24539375000006]
[35,0.34027777777777779,1000.000575]
[37.5,0.39062500000000006,1147.9598437500001]
[40,0.44444444444444442,1306.1232]
[42.5,0.50173611111111116,1474.4906437500001]
[45,0.5625,1653.062175]
[47.5,0.62673611111111105,1841.8377937499999]
[50,0.69444444444444453,2040.8175000000001]
[52.5,0.765625,2250.0012937500001]
[55,0.8402777777777779,2469.3891750000003]
[57.5,0.9184027777777779,2698.9811437500002]
[60,1,2938.7772]
[62.5,1,2938.7772]
[65,1,2938.7772]
[67.5,1,2938.7772]
[70,1,2938.7772]
[72.5,1,2938.7772]
[75,1,2938.7772]
[77.5,1,2938.7772]
[80,1,2938.7772]
[82.5,1,2938.7772]
[85,1,2938.7772]
[87.5,1,2938.7772]
[90,1,2938.7772]
[92.5,0.98782424285175485,2902.9953625000003]
[95,0.97574087957399436,2867.4850500000002]
[97.5,0.96373187545486605,2832.1932624999999]
[100,0.95179723049437037,2797.1200000000003]
[102.5,0.93993694469250677,2762.2652625000001]
[105,0.92815101804927569,2727.62905]
[107.5,0.91643945056467713,2693.2113625000002]
[110,0.90480224223871075,2659.0122000000001]
[112.5,0.8932393930713769,2625.0315625000003]
[115,0.88175090306267523,2591.2694500000002]
[117.5,0.87033677221260597,2557.7258624999999]
[120,0.85899700052116923,2524.4008000000003]
[122.5,0.84773158798836468,2491.2942625000001]
[125,0.83654053461419264,2458.40625]
[127.5,0.82542384039865291,2425.7367625000002]
[130,0.81438150534174558,2393.2858000000001]
[132.5,0.80341352944347066,2361.0533625000003]
[135,0.79251991270382804,2329.0394500000002]
[137.5,0.78170065512281772,2297.2440624999999]
[140,0.77095575670044003,2265.6672000000003]
[142.5,0.76028521743669442,2234.3088625]
[145,0.74968903733158132,2203.16905]
[147.5,0.73916721638510063,2172.2477625000001]
[150,0.72871975459725224,2141.5450000000001]
[152.5,0.71834665196803626,2111.0607625000002]
[155,0.70804790849745269,2080.7950500000002]
[157.5,0.69782352418550153,2050.7478625000003]
[160,0.68767349903218256,2020.9192]
[162.5,0.6775978330374961,1991.3090625000002]
[165,0.66759652620144194,1961.9174500000001]
[167.5,0.65766957852402019,1932.7443625000001]
[170,0.64781699000523074,1903.7898]
[172.5,0.63803876064507381,1875.0537625000002]
[175,0.62833489044354918,1846.5362500000001]
[177.5,0.61870537940065684,1818.2372625]
[180,0.60915022751639702,1790.1568000000002]
[182.5,0.59966943479076951,1762.2948625000001]
[185,0.59026300122377429,1734.6514500000001]
[187.5,0.58093092681541147,1707.2265625]
[190,0.57167321156568118,1680.0202000000002]
[192.5,0.56248985547458319,1653.0323625000001]
[195,0.55338085854211749,1626.26305]
[197.5,0.54434622076828421,1599.7122625000002]
[200,0.53538594215308333,1573.38]
[202.5,0.52650002269651475,1547.2662625]
[205,0.51768846239857869,1521.3710500000002]
[207.5,0.50895126125927481,1495.6943625000001]
[210,0.50028841927860335,1470.2362000000001]
[212.5,0.49169993645656429,1444.9965625]
[215,0.4831858127931577,1419.9754500000001]
[217.5,0.47474604828838335,1395.1728625000001]
[220,0.46638064294224141,1370.5888]
[222.5,0.45808959675473193,1346.2232625000001]
[225,0.4498729097258547,1322.0762500000001]
[227.5,0.44173058185560987,1298.1477625]
[230,0.43366261314399751,1274.4378000000002]
[232.5,0.42566900359101739,1250.9463625000001]
[235,0.41774975319666968,1227.67345]
[237.5,0.40990486196095444,1204.6190625000002]
[240,0.40213432988387143,1181.7832000000001]
[242.5,0.39443815696542084,1159.1658625]
[245,0.38681634320560271,1136.7670500000002]
[247.5,0.37926888860441688,1114.5867625000001]
[250,0.3717957931618634,1092.625]
[252.5,0.36439705687794233,1070.8817625000001]
[255,0.35707267975265361,1049.3570500000001]
[257.5,0.34982266178599725,1028.0508625]
[260,0.34264700297797329,1006.9632]
[262.5,0.33554570332858175,986.09406250000006]
[265,0.3285187628378225,965.4434500000001]
[267.5,0.32156618150569566,945.01136250000002]
[270,0.31468795933220117,924.79780000000005]
[272.5,0.3078840963173391,904.80276250000009]
[275,0.30115459246110932,885.02625]
[277.5,0.294499447763512,865.46826250000004]
[280,0.28791866222454704,846.12880000000007]
[282.5,0.28141223584421443,827.0078625000001]
[285,0.27498016862251418,808.10545000000002]
[287.5,0.26862246055944633,789.42156250000005]
[290,0.26233911165501084,770.95620000000008]
[292.5,0.2561301219092077,752.7093625]
[295,0.24999549132203694,734.68105000000003]
[297.5,0.24393521989349859,716.87126250000006]
[300,0.23794930762359259,699.28000000000009]
[302.5,0.23203775451231892,681.9072625]
[305,0.22620056055967769,664.75305000000003]
[307.5,0.22043772576566881,647.81736250000006]
[310,0.21474925013029231,631.10020000000009]
[312.5,0.20913513365354816,614.6015625]
[315,0.2035953763354364,598.32145000000003]
[317.5,0.19812997817595701,582.25986250000005]
[320,0.19273893917511001,566.41680000000008]
[322.5,0.18742225933289533,550.79226249999999]
[325,0.18217993864931306,535.38625000000002]
[327.5,0.17701197712436317,520.19876250000004]
[330,0.17191837475804564,505.22980000000001]
[332.5,0.16689913155036049,490.47936250000004]
[335,0.16195424750130769,475.94745]
[337.5,0.15708372261088729,461.63406250000003]
[340,0.15228755687909926,447.53920000000005]
[342.5,0.14756575030594357,433.66286250000002]
[345,0.1429183028914203,420.00505000000004]
[347.5,0.13834521463552937,406.56576250000001]
[350,0.13384648553827083,393.34500000000003]
[352.5,0.12942211559964467,380.34276250000005]
[355,0.12507210481965084,367.55905000000001]
[357.5,0.12079645319828942,354.99386250000003]
[360,0.11659516073556035,342.6472]
[362.5,0.11246822743146367,330.51906250000002]
[365,0.10841565328599938,318.60945000000004]
[367.5,0.10443743829916742,306.9183625]
[370,0.10053358247096786,295.44580000000002]
[372.5,9.6704085801400677E-2,284.19176250000004]
[375,9.2948948290465849E-2,273.15625]
[377.5,8.9268169938163403E-2,262.33926250000002]
[380,8.5661750744493323E-2,251.74080000000001]
[382.5,8.2129690709455624E-2,241.36086250000002]
[385,7.8671989833050293E-2,231.19945000000001]
[387.5,7.5288648115277329E-2,221.2565625]
[390,7.197966555613676E-2,211.53220000000002]
[392.5,6.8745042155628544E-2,202.0263625]
[395,6.5584777913752709E-2,192.73905000000002]
[397.5,6.2498872830509235E-2,183.67026250000001]
[400,5.9487326905898148E-2,174.82000000000002]
[402.5,5.6550140139919422E-2,166.18826250000001]
[405,5.3687312532573077E-2,157.77505000000002]
[407.5,5.0898844083859099E-2,149.58036250000001]
[410,4.8184734793777502E-2,141.60420000000002]
[412.5,4.5544984662328265E-2,133.8465625]
[415,4.297959368951141E-2,126.30745]
[417.5,4.0488561875326921E-2,118.9868625]
[420,3.8071889219774814E-2,111.88480000000001]
[422.5,3.5729575722855074E-2,105.00126250000001]
[425,3.3461621384567708E-2,98.336250000000007]
[427.5,3.1268026204912709E-2,91.889762500000003]
[430,2.9148790183890088E-2,85.661799999999999]
[432.5,2.7103913321499844E-2,79.65236250000001]
[435,2.5133395617741965E-2,73.861450000000005]
[437.5,2.3237237072616462E-2,68.2890625]
[440,2.1415437686123331E-2,62.935200000000002]
[442.5,1.9667997458262573E-2,57.799862500000003]
[445,1.799491638903419E-2,52.883050000000004]
[447.5,1.6396194478438177E-2,48.184762500000005]
[450,1.4871831726474537E-2,43.705000000000005]
[452.5,1.3421828133143269E-2,39.443762500000005]
[455,1.2046183698444375E-2,35.401050000000005]
[457.5,1.0744898422377852E-2,31.576862500000001]
[460,9.5179723049437035E-3,27.971200000000003]
[462.5,8.365405346141927E-3,24.584062500000002]
[465,7.287197545972522E-3,21.41545]
[467.5,6.2833489044354911E-3,18.465362500000001]
[470,5.3538594215308327E-3,15.7338]
[472.5,4.4987290972585475E-3,13.220762500000001]
[475,3.7179579316186343E-3,10.926250000000001]
[477.5,3.0115459246110939E-3,8.8502625000000013]
[480,2.3794930762359259E-3,6.9928000000000008]
[482.5,1.8217993864931305E-3,5.3538625]
[485,1.3384648553827082E-3,3.9334500000000001]
[487.5,9.2948948290465857E-4,2.7315625000000003]
[490,5.9487326905898147E-4,1.7482000000000002]
[492.5,3.3461621384567704E-4,0.98336250000000003]
[495,1.4871831726474537E-4,0.43705000000000005]
[497.5,3.7179579316186342E-5,0.10926250000000001]
[500,0,0]