{"text_format":"2","workbook":"xlsx","n_sheets":2,"sheets":["Input","Notes"],"not_rendered":{"charts":1,"images":1,"macros":1,"external_links":0,"defined_names":17,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Input","index":0,"n_rows":253,"n_cols":11,"rows_kept":253,"cut":false,"hidden":false,"merged":[[21,1,21,2],[4,1,4,2],[15,1,15,2],[11,1,11,2],[27,1,27,2]]}
[]
[{"$nulls":4},"Time (s)","Normalized","HRR (kW)",null,"Time (s)","Normalized","HRR (kW)"]
[{"$nulls":4},0,0,0,null,0,0,0]
[{"$nulls":4},1,0,0,null,10,0,0]
[null,"Input Parameters",null,null,2,0,0,null,46,6.0782399999999993E-2,60.782399999999996]
[null,"Peak HRR (kW)",1000,null,3,0,0,null,82,0.24312959999999997,243.12959999999998]
[null,"Initial Delay (s)",10,null,4,0,0,null,118,0.54704160000000002,547.04160000000002]
[null,"Growth Rate (α_g)",4.6899999999999997E-2,null,5,0,0,null,154,0.97251839999999989,972.51839999999993]
[null,"Peak Duration (s)",20,null,6,0,0,null,157,1,1000]
[null,"Decay Rate (α_d)",0.18759999999999999,null,7,0,0,null,176,1,1000]
[{"$nulls":4},8,0,0,null,194,0.58831359999999999,588.31359999999995]
[null,"Simplification Parameters",null,null,9,0,0,null,212,0.27089439999999998,270.89439999999996]
[null,"Growth Points",4,null,10,0,0,null,230,7.5039999999999996E-2,75.039999999999992]
[null,"Decay Points",4,null,11,4.6899999999999995E-5,4.6899999999999997E-2,null,248,7.5039999999999992E-4,0.75039999999999996]
[{"$nulls":4},12,1.8759999999999998E-4,0.18759999999999999,null,250,0,0]
[null,"Standard Alpha Values",null,null,13,4.2209999999999996E-4,0.42209999999999998]
[null,"Slow",2.9299999999999999E-3,null,14,7.5039999999999992E-4,0.75039999999999996]
[null,"Medium",1.172E-2,null,15,1.1724999999999999E-3,1.1724999999999999]
[null,"Fast",4.6899999999999997E-2,null,16,1.6883999999999998E-3,1.6883999999999999]
[null,"Ultrafast",0.18759999999999999,null,17,2.2981E-3,2.2980999999999998]
[{"$nulls":4},18,3.0015999999999997E-3,3.0015999999999998]
[null,"Total Heat Release",null,null,19,3.7988999999999996E-3,3.7988999999999997]
[null,"Raw Data (MJ)",93.982733299999992,null,20,4.6899999999999997E-3,4.6899999999999995]
[null,"Simplified Data (MJ)",95.922406400000014,null,21,5.6749000000000001E-3,5.6749000000000001]
[null,"Difference [S-R] (MJ)",{"$f":"(_hrSimpTot-_hrRawTot)","v":1.9396731000000216},null,22,6.7535999999999994E-3,6.7535999999999996]
[null,"% Difference [S/R]",{"$f":"_hrSimpTot/_hrRawTot","v":1.0206386112841435},null,23,7.9261000000000002E-3,7.9260999999999999]
[{"$nulls":4},24,9.1923999999999999E-3,9.1923999999999992]
[null,"Curve Data",null,null,25,1.0552499999999999E-2,10.5525]
[null,"t_0",10,null,26,1.2006399999999999E-2,12.006399999999999]
[null,"t_1MW",157,null,27,1.3554099999999999E-2,13.5541]
[null,"t_l0",157,null,28,1.5195599999999998E-2,15.195599999999999]
[null,"t_d",176,null,29,1.6930899999999999E-2,16.930899999999998]
[null,"t_end",250,null,30,1.8759999999999999E-2,18.759999999999998]
[null,"Q-dot_max",{"$f":"_peakHRR","v":1000},null,31,2.0682900000000001E-2,20.6829]
[null,"t_g",{"$f":"_t1MW-_t0","v":147},null,32,2.26996E-2,22.6996]
[null,"a_g",{"$f":"_alphaG","v":4.6899999999999997E-2},null,33,2.4810099999999998E-2,24.810099999999998]
[null,"d_g",{"$f":"_alphaD","v":0.18759999999999999},null,34,2.7014399999999997E-2,27.014399999999998]
[{"$nulls":4},35,2.9312499999999998E-2,29.3125]
[{"$nulls":4},36,3.1704400000000001E-2,31.7044]
[{"$nulls":4},37,3.4190100000000001E-2,34.190100000000001]
[{"$nulls":4},38,3.67696E-2,36.769599999999997]
[{"$nulls":4},39,3.9442899999999996E-2,39.442899999999995]
[{"$nulls":4},40,4.2209999999999998E-2,42.21]
[{"$nulls":4},41,4.5070899999999997E-2,45.070899999999995]
[{"$nulls":4},42,4.8025599999999995E-2,48.025599999999997]
[{"$nulls":4},43,5.1074099999999997E-2,51.074099999999994]
[{"$nulls":4},44,5.4216399999999998E-2,54.2164]
[{"$nulls":4},45,5.7452499999999997E-2,57.452499999999993]
[{"$nulls":4},46,6.0782399999999993E-2,60.782399999999996]
[{"$nulls":4},47,6.4206099999999988E-2,64.206099999999992]
[{"$nulls":4},48,6.7723599999999995E-2,67.72359999999999]
[{"$nulls":4},49,7.1334899999999993E-2,71.33489999999999]
[{"$nulls":4},50,7.5039999999999996E-2,75.039999999999992]
[{"$nulls":4},51,7.883889999999999E-2,78.838899999999995]
[{"$nulls":4},52,8.2731600000000002E-2,82.7316]
[{"$nulls":4},53,8.6718099999999992E-2,86.718099999999993]
[{"$nulls":4},54,9.0798400000000001E-2,90.798400000000001]
[{"$nulls":4},55,9.4972500000000001E-2,94.972499999999997]
[{"$nulls":4},56,9.9240399999999993E-2,99.240399999999994]
[{"$nulls":4},57,0.10360209999999999,103.60209999999999]
[{"$nulls":4},58,0.10805759999999999,108.05759999999999]
[{"$nulls":4},59,0.1126069,112.6069]
[{"$nulls":4},60,0.11724999999999999,117.25]
[{"$nulls":4},61,0.1219869,121.98689999999999]
[{"$nulls":4},62,0.1268176,126.8176]
[{"$nulls":4},63,0.1317421,131.74209999999999]
[{"$nulls":4},64,0.1367604,136.7604]
[{"$nulls":4},65,0.14187250000000001,141.8725]
[{"$nulls":4},66,0.1470784,147.07839999999999]
[{"$nulls":4},67,0.15237809999999999,152.37809999999999]
[{"$nulls":4},68,0.15777159999999998,157.77159999999998]
[{"$nulls":4},69,0.16325889999999998,163.25889999999998]
[{"$nulls":4},70,0.16883999999999999,168.84]
[{"$nulls":4},71,0.17451489999999997,174.51489999999998]
[{"$nulls":4},72,0.18028359999999999,180.28359999999998]
[{"$nulls":4},73,0.18614609999999998,186.14609999999999]
[{"$nulls":4},74,0.19210239999999998,192.10239999999999]
[{"$nulls":4},75,0.19815249999999998,198.15249999999997]
[{"$nulls":4},76,0.20429639999999999,204.29639999999998]
[{"$nulls":4},77,0.2105341,210.5341]
[{"$nulls":4},78,0.21686559999999999,216.8656]
[{"$nulls":4},79,0.22329089999999999,223.29089999999999]
[{"$nulls":4},80,0.22980999999999999,229.80999999999997]
[{"$nulls":4},81,0.23642289999999999,236.4229]
[{"$nulls":4},82,0.24312959999999997,243.12959999999998]
[{"$nulls":4},83,0.24993009999999999,249.93009999999998]
[{"$nulls":4},84,0.25682439999999995,256.82439999999997]
[{"$nulls":4},85,0.26381250000000001,263.8125]
[{"$nulls":4},86,0.27089439999999998,270.89439999999996]
[{"$nulls":4},87,0.27807009999999999,278.07009999999997]
[{"$nulls":4},88,0.28533959999999997,285.33959999999996]
[{"$nulls":4},89,0.29270289999999999,292.7029]
[{"$nulls":4},90,0.30015999999999998,300.15999999999997]
[{"$nulls":4},91,0.30771089999999995,307.71089999999998]
[{"$nulls":4},92,0.31535559999999996,315.35559999999998]
[{"$nulls":4},93,0.3230941,323.09409999999997]
[{"$nulls":4},94,0.33092640000000001,330.9264]
[{"$nulls":4},95,0.33885249999999995,338.85249999999996]
[{"$nulls":4},96,0.34687239999999997,346.87239999999997]
[{"$nulls":4},97,0.35498609999999997,354.98609999999996]
[{"$nulls":4},98,0.36319360000000001,363.1936]
[{"$nulls":4},99,0.37149489999999996,371.49489999999997]
[{"$nulls":4},100,0.37989000000000001,379.89]
[{"$nulls":4},101,0.38837889999999997,388.37889999999999]
[{"$nulls":4},102,0.39696159999999997,396.96159999999998]
[{"$nulls":4},103,0.40563809999999995,405.63809999999995]
[{"$nulls":4},104,0.41440839999999995,414.40839999999997]
[{"$nulls":4},105,0.4232725,423.27249999999998]
[{"$nulls":4},106,0.43223039999999996,432.23039999999997]
[{"$nulls":4},107,0.44128209999999995,441.28209999999996]
[{"$nulls":4},108,0.45042759999999998,450.42759999999998]
[{"$nulls":4},109,0.45966689999999999,459.6669]
[{"$nulls":4},110,0.46899999999999997,469]
[{"$nulls":4},111,0.47842689999999999,478.42689999999999]
[{"$nulls":4},112,0.48794759999999998,487.94759999999997]
[{"$nulls":4},113,0.49756210000000001,497.56209999999999]
[{"$nulls":4},114,0.50727040000000001,507.2704]
[{"$nulls":4},115,0.51707250000000005,517.07249999999999]
[{"$nulls":4},116,0.5269684,526.96839999999997]
[{"$nulls":4},117,0.53695809999999999,536.95809999999994]
[{"$nulls":4},118,0.54704160000000002,547.04160000000002]
[{"$nulls":4},119,0.55721889999999996,557.21889999999996]
[{"$nulls":4},120,0.56749000000000005,567.49]
[{"$nulls":4},121,0.57785489999999995,577.85489999999993]
[{"$nulls":4},122,0.58831359999999999,588.31359999999995]
[{"$nulls":4},123,0.59886609999999996,598.86609999999996]
[{"$nulls":4},124,0.60951239999999995,609.51239999999996]
[{"$nulls":4},125,0.62025249999999998,620.25249999999994]
[{"$nulls":4},126,0.63108639999999994,631.08639999999991]
[{"$nulls":4},127,0.64201410000000003,642.01409999999998]
[{"$nulls":4},128,0.65303559999999994,653.03559999999993]
[{"$nulls":4},129,0.66415089999999999,664.15089999999998]
[{"$nulls":4},130,0.67535999999999996,675.36]
[{"$nulls":4},131,0.68666289999999996,686.66289999999992]
[{"$nulls":4},132,0.69805959999999989,698.05959999999993]
[{"$nulls":4},133,0.70955009999999996,709.55009999999993]
[{"$nulls":4},134,0.72113439999999995,721.13439999999991]
[{"$nulls":4},135,0.73281249999999998,732.8125]
[{"$nulls":4},136,0.74458439999999992,744.58439999999996]
[{"$nulls":4},137,0.7564500999999999,756.45009999999991]
[{"$nulls":4},138,0.76840959999999991,768.40959999999995]
[{"$nulls":4},139,0.78046289999999996,780.46289999999999]
[{"$nulls":4},140,0.79260999999999993,792.6099999999999]
[{"$nulls":4},141,0.80485089999999992,804.85089999999991]
[{"$nulls":4},142,0.81718559999999996,817.18559999999991]
[{"$nulls":4},143,0.82961410000000002,829.61410000000001]
[{"$nulls":4},144,0.84213640000000001,842.13639999999998]
[{"$nulls":4},145,0.85475249999999992,854.75249999999994]
[{"$nulls":4},146,0.86746239999999997,867.4624]
[{"$nulls":4},147,0.88026609999999994,880.26609999999994]
[{"$nulls":4},148,0.89316359999999995,893.16359999999997]
[{"$nulls":4},149,0.90615489999999999,906.1549]
[{"$nulls":4},150,0.91923999999999995,919.2399999999999]
[{"$nulls":4},151,0.93241889999999994,932.41889999999989]
[{"$nulls":4},152,0.94569159999999997,945.69159999999999]
[{"$nulls":4},153,0.95905809999999991,959.05809999999997]
[{"$nulls":4},154,0.97251839999999989,972.51839999999993]
[{"$nulls":4},155,0.98607250000000002,986.07249999999999]
[{"$nulls":4},156,0.99972039999999995,999.72039999999993]
[{"$nulls":4},157,1,1000]
[{"$nulls":4},158,1,1000]
[{"$nulls":4},159,1,1000]
[{"$nulls":4},160,1,1000]
[{"$nulls":4},161,1,1000]
[{"$nulls":4},162,1,1000]
[{"$nulls":4},163,1,1000]
[{"$nulls":4},164,1,1000]
[{"$nulls":4},165,1,1000]
[{"$nulls":4},166,1,1000]
[{"$nulls":4},167,1,1000]
[{"$nulls":4},168,1,1000]
[{"$nulls":4},169,1,1000]
[{"$nulls":4},170,1,1000]
[{"$nulls":4},171,1,1000]
[{"$nulls":4},172,1,1000]
[{"$nulls":4},173,1,1000]
[{"$nulls":4},174,1,1000]
[{"$nulls":4},175,1,1000]
[{"$nulls":4},176,1,1000]
[{"$nulls":4},177,0.99972039999999995,999.72039999999993]
[{"$nulls":4},178,0.97251839999999989,972.51839999999993]
[{"$nulls":4},179,0.94569159999999997,945.69159999999999]
[{"$nulls":4},180,0.91923999999999995,919.2399999999999]
[{"$nulls":4},181,0.89316359999999995,893.16359999999997]
[{"$nulls":4},182,0.86746239999999997,867.4624]
[{"$nulls":4},183,0.84213640000000001,842.13639999999998]
[{"$nulls":4},184,0.81718559999999996,817.18559999999991]
[{"$nulls":4},185,0.79260999999999993,792.6099999999999]
[{"$nulls":4},186,0.76840959999999991,768.40959999999995]
[{"$nulls":4},187,0.74458439999999992,744.58439999999996]
[{"$nulls":4},188,0.72113439999999995,721.13439999999991]
[{"$nulls":4},189,0.69805959999999989,698.05959999999993]
[{"$nulls":4},190,0.67535999999999996,675.36]
[{"$nulls":4},191,0.65303559999999994,653.03559999999993]
[{"$nulls":4},192,0.63108639999999994,631.08639999999991]
[{"$nulls":4},193,0.60951239999999995,609.51239999999996]
[{"$nulls":4},194,0.58831359999999999,588.31359999999995]
[{"$nulls":4},195,0.56749000000000005,567.49]
[{"$nulls":4},196,0.54704160000000002,547.04160000000002]
[{"$nulls":4},197,0.5269684,526.96839999999997]
[{"$nulls":4},198,0.50727040000000001,507.2704]
[{"$nulls":4},199,0.48794759999999998,487.94759999999997]
[{"$nulls":4},200,0.46899999999999997,469]
[{"$nulls":4},201,0.45042759999999998,450.42759999999998]
[{"$nulls":4},202,0.43223039999999996,432.23039999999997]
[{"$nulls":4},203,0.41440839999999995,414.40839999999997]
[{"$nulls":4},204,0.39696159999999997,396.96159999999998]
[{"$nulls":4},205,0.37989000000000001,379.89]
[{"$nulls":4},206,0.36319360000000001,363.1936]
[{"$nulls":4},207,0.34687239999999997,346.87239999999997]
[{"$nulls":4},208,0.33092640000000001,330.9264]
[{"$nulls":4},209,0.31535559999999996,315.35559999999998]
[{"$nulls":4},210,0.30015999999999998,300.15999999999997]
[{"$nulls":4},211,0.28533959999999997,285.33959999999996]
[{"$nulls":4},212,0.27089439999999998,270.89439999999996]
[{"$nulls":4},213,0.25682439999999995,256.82439999999997]
[{"$nulls":4},214,0.24312959999999997,243.12959999999998]
[{"$nulls":4},215,0.22980999999999999,229.80999999999997]
[{"$nulls":4},216,0.21686559999999999,216.8656]
[{"$nulls":4},217,0.20429639999999999,204.29639999999998]
[{"$nulls":4},218,0.19210239999999998,192.10239999999999]
[{"$nulls":4},219,0.18028359999999999,180.28359999999998]
[{"$nulls":4},220,0.16883999999999999,168.84]
[{"$nulls":4},221,0.15777159999999998,157.77159999999998]
[{"$nulls":4},222,0.1470784,147.07839999999999]
[{"$nulls":4},223,0.1367604,136.7604]
[{"$nulls":4},224,0.1268176,126.8176]
[{"$nulls":4},225,0.11724999999999999,117.25]
[{"$nulls":4},226,0.10805759999999999,108.05759999999999]
[{"$nulls":4},227,9.9240399999999993E-2,99.240399999999994]
[{"$nulls":4},228,9.0798400000000001E-2,90.798400000000001]
[{"$nulls":4},229,8.2731600000000002E-2,82.7316]
[{"$nulls":4},230,7.5039999999999996E-2,75.039999999999992]
[{"$nulls":4},231,6.7723599999999995E-2,67.72359999999999]
[{"$nulls":4},232,6.0782399999999993E-2,60.782399999999996]
[{"$nulls":4},233,5.4216399999999998E-2,54.2164]
[{"$nulls":4},234,4.8025599999999995E-2,48.025599999999997]
[{"$nulls":4},235,4.2209999999999998E-2,42.21]
[{"$nulls":4},236,3.67696E-2,36.769599999999997]
[{"$nulls":4},237,3.1704400000000001E-2,31.7044]
[{"$nulls":4},238,2.7014399999999997E-2,27.014399999999998]
[{"$nulls":4},239,2.26996E-2,22.6996]
[{"$nulls":4},240,1.8759999999999999E-2,18.759999999999998]
[{"$nulls":4},241,1.5195599999999998E-2,15.195599999999999]
[{"$nulls":4},242,1.2006399999999999E-2,12.006399999999999]
[{"$nulls":4},243,9.1923999999999999E-3,9.1923999999999992]
[{"$nulls":4},244,6.7535999999999994E-3,6.7535999999999996]
[{"$nulls":4},245,4.6899999999999997E-3,4.6899999999999995]
[{"$nulls":4},246,3.0015999999999997E-3,3.0015999999999998]
[{"$nulls":4},247,1.6883999999999998E-3,1.6883999999999999]
[{"$nulls":4},248,7.5039999999999992E-4,0.75039999999999996]
[{"$nulls":4},249,1.8759999999999998E-4,0.18759999999999999]
[{"$nulls":4},250,0,0]

{"sheet":"Notes","index":1,"n_rows":6,"n_cols":2,"rows_kept":6,"cut":false,"hidden":false,"merged":[[4,1,4,8]]}
[]
[null,"To verify the growth curve, enter a peak HRR of 100, 5 second Initial Delay, growth rate of \"Fast\"."]
[null,"The calculator on this page rounds up to the next second, so the time to Peak HRR here is 52 seconds."]
[null,"Then, visit the link below, you will see that the 100 kW crossing point is at 51.176 seconds."]
[null,"https://www.desmos.com/calculator/olelki8mag"]
[null,"You can alter the inputs here and on that site  to test different combinations."]