{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Input","Data","Output"],"not_rendered":{"charts":1,"images":2,"macros":1,"external_links":0,"defined_names":13,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Input","index":0,"n_rows":21,"n_cols":7,"rows_kept":21,"cut":false,"hidden":false,"merged":[[12,1,12,2],[18,1,18,6],[12,3,12,6],[11,1,11,6]]}
[]
["Calculates HRR for different fires using a t2 fire for growth and decay periods, with a constant max between these two periods."]
[null,"Ref: Heat Release Rates of Burning Items in Fires, Hyeong-Jin Kim and David G. Lilley, AIAA 2000-0722, 38th Aerospace Sciences Meeting & Exhibit, 10-13 January 2000, Reno, NV."]
{"$rows_empty":8}
[null,"Select fire type"]
[null,"Fire Type: ",null,"Chair 6 - FASTLite"]
[null,null,"Divisions in Graph:",200]
[]
[]
[]
[]
[null,"Parameters in Calculations (Do not edit)"]
[null,"t0","tl0","td","tend","αg","αd"]
[null,0,70,90,315,0.4,3.8716E-2]

{"sheet":"Data","index":1,"n_rows":67,"n_cols":12,"rows_kept":67,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Name","Description","t0","t1 MW","tl0","td","tend","Q-dotmax","tg","αg","αd"]
[null,"Wardrobe 1 - FASTLite","1/2\" Plywood wardrobe,  clothing on 16 hangers ",0,35,60,90,500,2938.8,35,0.81632700000000002,1.7482000000000001E-2]
[null,"Wardrobe 2 - FASTLite","1/8\" Plywood wardrobe,  clothing on 16 hangers ",0,40,100,110,140,6250,40,0.625,6.9444439999999998]
[null,"Wardrobe 3 - FASTLite","1/8\" Plywood wardrobe,  FR paint, clothing on 16 hangers ",0,30,70,80,400,5444.4,30,1.111111,5.3168E-2]
[null,"Wardrobe 4 - FASTLite","1/8\" Plywood wardrobe,  FR paint, clothing on 16 hangers ",0,90,150,160,450,2777.8,90,0.123457,3.3029000000000003E-2]
[null,"Wardrobe 5 - FASTLite","3/4\" Particle-board wardrobe,  thin plastic coating ",0,150,170,670,2000,1284.4000000000001,150,4.4443999999999997E-2,7.2599999999999997E-4]
[null,"Chair 1 - FASTLite","Chair, one-piece wood-reinforced urethane foam",0,1000,650,660,1900,422.5,1000,1E-3,2.7500000000000002E-4]
[null,"Chair 2 - FASTLite","Chair, polypropylene foam frame, urethane foam, polyolefin fabric",0,100,140,160,500,1960,100,0.1,1.6955000000000001E-2]
[null,"Chair 3 - FASTLite","Chair, thin wood frame, California foam, polyolefin fabric",0,200,175,176,900,765.6,200,2.5000000000000001E-2,1.4610000000000001E-3]
[null,"Chair 4 - FASTLite","Chair, urethane foam frame, urethane foam, polyolefin fabric",0,60,60,210,430,1000,60,0.27777800000000002,2.0660999999999999E-2]
[null,"Chair 5 - FASTLite","Chair, wood frame, California foam, Haitian cotton fabric",0,350,275,475,1000,617.29999999999995,350,8.1630000000000001E-3,2.2399999999999998E-3]
[null,"Chair 6 - FASTLite","Chair, wood frame, California foam, polyolefin fabric",0,50,70,90,315,1960,50,0.4,3.8716E-2]
[null,"Chair 7 - FASTLite","Chair, wood frame, FR cotton stuffing, Haitian cotton fabric",0,2000,210,310,1000,11,2000,2.5000000000000001E-4,2.3E-5]
[null,"Chair 8 - FASTLite","Chair, wood frame, FR cotton stuffing, polyolefin fabric",0,400,275,475,1000,472.7,400,6.2500000000000003E-3,1.7149999999999999E-3]
[null,"Chair 9 - FASTLite","Chair, wood frame, urethane foam, cotton fabric",0,200,90,310,550,202.5,200,2.5000000000000001E-2,3.516E-3]
[null,"Chair 10 - FASTLite","Chair, wood frame, urethane foam, cotton fabric",0,75,50,250,1250,444.4,75,0.17777799999999999,4.44E-4]
[null,"Chair 11 - FASTLite","Chair, wood frame, urethane foam, cotton fabric, polyester batting",0,425,347,367,1000,666.6,425,5.5360000000000001E-3,1.6639999999999999E-3]
[null,"Chair 12 - FASTLite","Chair, wood frame, urethane foam, polyolefin fabric",0,80,160,170,420,4000,80,0.15625,6.4000000000000001E-2]
[null,"Chair 13 - FASTLite","Chair, wood frame, urethane foam, quilted cotton/plyolefin, polyester batting",0,200,187,200,500,874.2,200,2.5000000000000001E-2,9.7140000000000004E-3]
[null,"Bed - FASTLite Data","Innerspring mattress and boxspring, cotton felt/urethane/sisal cover",0,1100,680,1080,1300,382.1,1100,8.2600000000000002E-4,7.8960000000000002E-3]
[null,"Lounge chair 1 - FASTLite Data","Lounge chair, metal frame, urethane foam, plastic-coated fabric",0,350,170,220,350,235.9,350,8.1630000000000001E-3,1.396E-2]
[null,"Lounge chair 2 - FASTLite Data","Lounge chair, one-piece molded glass fiber, metal legs",0,120,20,21,150,27.8,120,6.9444000000000006E-2,1.6689999999999999E-3]
[null,"Lounge chair 3 - FASTLite Data","Lounge chair, one-piece molded thermoplastic",0,275,230,430,900,699.5,275,1.3223E-2,3.1670000000000001E-3]
[null,"Lounge chair 4 - FASTLite Data","Lounge chair, wood frame, latex foam/cotton stuffing, plastic-coated fabric ",0,500,130,140,300,67.599999999999994,500,4.0000000000000001E-3,2.6410000000000001E-3]
[null,"Loveseat 1 - FASTLite Data","Loveseat, mixed foam and cotton batting stuffing, cotton fabric ",0,400,350,400,2000,765.6,400,6.2500000000000003E-3,2.99E-4]
[null,"Loveseat 2 - FASTLite Data","Loveseat, wood frame, California foam, polyolefin fabric ",0,80,130,160,400,2640.6,80,0.15625,4.5844000000000003E-2]
[null,"Loveseat 3 - FASTLite Data","Loveseat, wood frame, urethane foam, plastic-coated fabric ",0,350,330,430,1500,889,350,8.1630000000000001E-3,7.76E-4]
[null,"Metal wardrobe 1 - FASTLite Data","Metal wardrobe, clothing on 16 hangers ",0,250,125,150,500,250,250,1.6E-2,2.0409999999999998E-3]
[null,"Metal wardrobe 2 - FASTLite Data","Metal wardrobe, clothing on 8 hangers ",0,50,40,47,200,640,50,0.4,2.734E-2]
[null,"Patient lounge chair - FASTLite Data","Patient lounge chair, metal frame, urethane foam cushion ",0,170,80,90,150,221.5,170,3.4602000000000001E-2,6.1515E-2]
[null,"Sofa 1 - FASTLite Data","Sofa, metal frame, urethane foam, plastic-coated fabric ",0,500,260,460,800,270.39999999999998,500,4.0000000000000001E-3,2.3389999999999999E-3]
[null,"Sofa 2 - FASTLite Data","Sofa, wood frame, California foam, polyolefin fabric ",0,100,170,250,430,2890,100,0.1,8.9198E-2]
[null,"F21 Chair - FASTLite Data","F21 Chair, wood frame, polyurethane foam, olefin fabric ",140,215,250,250,360,2151.1,75,0.17777799999999999,0.17777799999999999]
[null,"F31 Loveseat - FASTLite Data","F31 Loveseat, wood frame, polyurethane foam, olefin fabric ",90,165,215,265,390,2777.8,75,0.17777799999999999,0.17777799999999999]
[null,"F32 Sofa - FASTLite Data","F32 Sofa, wood frame, polyurethane foam, olefin fabric ",75,150,205,270,400,3004.4,75,0.17777799999999999,0.17777799999999999]
[null,"Bed 1 - HAZARD Data","Double bed, bedding, night table, gypsum bd walls",169,211,230,230,936,2109.4,42,0.56689299999999998,4.2319999999999997E-3]
[null,"Bed 2 - HAZARD Data","Double bed, bedding, night table, plywood walls",164,239,360,430,998,6829.5,75,0.17777799999999999,2.1169E-2]
[null,"Chair 1 (F21) - HAZARD Data","Upholstered chair,F21 , wood frame, pu foam-fr, olefin ",126,218,260,260,607,2121.5,92,0.118147,1.7618999999999999E-2]
[null,"Chair 2 (F23) - HAZARD Data","Chair, F23,wood frame, fr cotton batting,olefin ",0,538,450,450,1932,699.6,538,3.4550000000000002E-3,3.19E-4]
[null,"Chair 3 (F25) - HAZARD Data","Upholstered chair, F25, wood frame, pu foam, olefin",106,215,260,260,679,1996.1,109,8.4168000000000007E-2,1.137E-2]
[null,"Chair 4 (F28) - HAZARD Data","Upholstered chair, F28, wood frame, pu/pe/ctn bedding, cotton",82,478,420,420,1184,728.5,396,6.3769999999999999E-3,1.248E-3]
[null,"Chair 5 (F30) - HAZARD Data","Upholstered chair, F30, pu frame, pu foam, olefin",40,140,130,263,1017,810,100,0.1,1.4250000000000001E-3]
[null,"Chair 6 - HAZARD Data","Bean bag chair, vinyl/ps foam beads",88,748,545,718,1228,479.5,660,2.2959999999999999E-3,1.843E-3]
[null,"Chair 7 - HAZARD Data","Char, molded flexible pu frame, pu cover ",644,1662,1330,1330,2685,454.1,1018,9.6500000000000004E-4,2.4699999999999999E-4]
[null,"Chair 8 - HAZARD Data","Easy chair, molded ps foam frame,pu pad and cover ",38,245,240,240,883,952.3,207,2.3338000000000001E-2,2.3029999999999999E-3]
[null,"Christmas Tree - HAZARD Data","Christmas tree, spruce, dry ",290,327,320,350,478,657.4,37,0.73046,4.0125000000000001E-2]
[null,"Cooking Oil - HAZARD Data","Cooking, Corn, Cottonseed, Etc in 12inch pan ",0,15,5,1000,1000,111.1,15,4.4444439999999998]
[null,"Curtain - HAZARD Data","Curtain, Cotton, 0.31 kg/m2",123,229,175,175,411,240.7,106,8.8999999999999996E-2,4.3210000000000002E-3]
[null,"Loveseat (F31) - HAZARD Data","Loveseat, F31, wood frame, pu foam(fr), olefin ",71,165,229,249,701,2825.3,94,0.113173,1.3828999999999999E-2]
[null,"Mattress 1 - HAZARD Data","Mattress, m05, wood frame, pu foam, rayon ticking, bedding ",269,437,480,480,933,1577.4,168,3.5430999999999997E-2,7.6870000000000003E-3]
[null,"Mattress 2 - HAZARD Data","Mattress and boxspring (westchase hilton) ",144,858,606,980,2233,418.7,714,1.9620000000000002E-3,2.6699999999999998E-4]
[null,"Sofa (F32) - HAZARD Data","Upholstered/sofa, F32, wood\\frame, pu foam-fr,olefin",74,154,211,283,651,2932.7,80,0.15625,2.1655000000000001E-2]
[null,"Trash Bags - HAZARD Data","Trash bags (3), paper ",0,100,58,111,517,336.4,100,0.1,2.0409999999999998E-3]
[null,"TV Set - HAZARD Data","Television set, b/w, wood cabinet ",304,984,670,670,1872,289.7,680,2.163E-3,2.0100000000000001E-4]
[null,"Wardrobe - HAZARD Data","Wardrobe closet, plywood, fr paint ",70,113,170,170,358,5408.3,43,0.54083300000000001,0.15301999999999999]
[null,"Waste Basket - HAZARD Data","Wastepaper baskete, polythylene, milk cartons ",115,2034,350,350,1264,15,1919,2.72E-4,1.8E-5]
[null,"Bunk Bed - BFRL Data","BFRL in February 1996. ",186,211,240,240,445,4665.6000000000004,25,1.6,0.11101999999999999]
[null,"Koisk - BFRL Data","Western Fire Center in the summer of 1995 ",817,1129,1230,1230,3300,1752.2,312,1.0272999999999999E-2,4.0900000000000002E-4]
[null,"Loveseat - BFRL Data",null,48,222,350,371,866,3012.4,174,3.3029000000000003E-2,1.2293999999999999E-2]
[null,"Mattress (Center) - BFRL Data","BFRL in February 1996. ",9,173,145,219,959,687.7,164,3.7179999999999998E-2,1.256E-3]
[null,"Mattress (Corner) - BFRL Data","BFRL in February 1996. ",85,294,295,321,484,1009.6,209,2.2893E-2,3.7998999999999998E-2]
[null,"Small Dresser - BFRL Data","BFRL in February 1996 ",112,346,423,423,870,1766.4,234,1.8263000000000001E-2,8.8400000000000006E-3]
[null,"Sofa - BFRL Data",null,26,222,390,399,931,3449,196,2.6030999999999999E-2,1.2186000000000001E-2]
[null,"Wooden Pallet - BFRL Data","BFRL in February 1996. ",0,467,634,664,1616,1843.1,467,4.5849999999999997E-3,2.0339999999999998E-3]
[null,"Workstation (2 panels) - BFRL Data","Sponsored by GSA and performed at BFRL in 1991 ",132,244,280,280,3276,1746.2,112,7.9718999999999998E-2,1.95E-4]
[null,"Workstation (3 panels) - BFRL Data","Sponsored by GSA and performed at BFRL in 1991.  ",283,386,550,550,1142,6719.7,103,9.4259999999999997E-2,1.9174E-2]

{"sheet":"Output","index":2,"n_rows":204,"n_cols":3,"rows_kept":204,"cut":false,"hidden":false,"merged":[]}
[null,"HRR Max (kW) =",1960]
[null,"Total Heat Release (MJ) =",231.92852404752858]
["Time (s)","Normalized","HRR (kW)"]
[0,0,0]
[1.575,5.0624999999999997E-4,0.99224999999999997]
[3.15,2.0249999999999999E-3,3.9689999999999999]
[4.7249999999999996,4.5562499999999995E-3,8.9302499999999991]
[6.3,8.0999999999999996E-3,15.875999999999999]
[7.875,1.2656250000000001E-2,24.806250000000002]
[9.4499999999999993,1.8224999999999998E-2,35.720999999999997]
[11.024999999999999,2.4806249999999995E-2,48.620249999999992]
[12.599999999999998,3.2399999999999991E-2,63.503999999999976]
[14.174999999999997,4.100624999999998E-2,80.372249999999966]
[15.749999999999996,5.0624999999999983E-2,99.224999999999966]
[17.324999999999996,6.1256249999999977E-2,120.06224999999995]
[18.899999999999995,7.2899999999999965E-2,142.88399999999993]
[20.474999999999994,8.5556249999999959E-2,167.69024999999991]
[22.049999999999994,9.9224999999999938E-2,194.48099999999988]
[23.624999999999993,0.11390624999999995,223.25624999999988]
[25.199999999999992,0.12959999999999991,254.01599999999985]
[26.774999999999991,0.14630624999999992,286.76024999999981]
[28.349999999999991,0.16402499999999989,321.48899999999981]
[29.92499999999999,0.1827562499999999,358.20224999999982]
[31.499999999999989,0.20249999999999987,396.89999999999975]
[33.074999999999989,0.22325624999999985,437.5822499999997]
[34.649999999999991,0.24502499999999991,480.2489999999998]
[36.224999999999994,0.26780624999999997,524.90024999999991]
[37.799999999999997,0.29159999999999997,571.53599999999994]
[39.375,0.31640625,620.15625]
[40.950000000000003,0.34222500000000006,670.76100000000008]
[42.525000000000006,0.36905625000000014,723.3502500000003]
[44.100000000000009,0.3969000000000002,777.92400000000043]
[45.675000000000011,0.42575625000000022,834.48225000000048]
[47.250000000000014,0.45562500000000028,893.02500000000055]
[48.825000000000017,0.48650625000000031,953.55225000000064]
[50.40000000000002,0.51840000000000042,1016.0640000000009]
[51.975000000000023,0.55130625000000055,1080.5602500000011]
[53.550000000000026,0.58522500000000055,1147.0410000000011]
[55.125000000000028,0.62015625000000063,1215.5062500000013]
[56.700000000000031,0.65610000000000079,1285.9560000000015]
[58.275000000000034,0.69305625000000093,1358.3902500000017]
[59.850000000000037,0.73102500000000104,1432.809000000002]
[61.42500000000004,0.77000625000000111,1509.2122500000021]
[63.000000000000043,0.81000000000000116,1587.6000000000022]
[64.575000000000045,0.85100625000000119,1667.9722500000023]
[66.150000000000048,0.8930250000000014,1750.3290000000027]
[67.725000000000051,0.93605625000000148,1834.6702500000029]
[69.300000000000054,0.98010000000000141,1920.9960000000028]
[70.875000000000057,1,1960]
[72.45000000000006,1,1960]
[74.025000000000063,1,1960]
[75.600000000000065,1,1960]
[77.175000000000068,1,1960]
[78.750000000000071,1,1960]
[80.325000000000074,1,1960]
[81.900000000000077,1,1960]
[83.47500000000008,1,1960]
[85.050000000000082,1,1960]
[86.625000000000085,1,1960]
[88.200000000000088,1,1960]
[89.775000000000091,1,1960]
[91.350000000000094,0.98803473974999934,1936.5480899099987]
[92.925000000000097,0.97416775743749917,1909.3688045774984]
[94.500000000000099,0.96039877499999893,1882.381598999998]
[96.075000000000102,0.94672779243749916,1855.5864731774984]
[97.650000000000105,0.9331548097499992,1828.9834271099985]
[99.225000000000108,0.91967982693749906,1802.5724607974983]
[100.80000000000011,0.90630284399999905,1776.3535742399981]
[102.37500000000011,0.89302386093749908,1750.3267674374981]
[103.95000000000012,0.87984287774999925,1724.4920403899985]
[105.52500000000012,0.86675989443749901,1698.849393097498]
[107.10000000000012,0.85377491099999891,1673.3988255599979]
[108.67500000000013,0.84088792743749896,1648.140337777498]
[110.25000000000013,0.82809894374999915,1623.0739297499983]
[111.82500000000013,0.81540795993749893,1598.1996014774979]
[113.40000000000013,0.80281497599999885,1573.5173529599977]
[114.97500000000014,0.7903199919374988,1549.0271841974977]
[116.55000000000014,0.77792300774999901,1524.7290951899981]
[118.12500000000014,0.76562402343749891,1500.6230859374978]
[119.70000000000014,0.75342303899999874,1476.7091564399975]
[121.27500000000015,0.74132005443749893,1452.9873066974978]
[122.85000000000015,0.72931506974999905,1429.4575367099981]
[124.42500000000015,0.71740808493749897,1406.119846477498]
[126.00000000000016,0.7055990999999987,1382.9742359999975]
[127.57500000000016,0.6938881149374988,1360.0207052774977]
[129.15000000000015,0.68227512974999893,1337.2592543099979]
[130.72500000000014,0.67076014443749898,1314.6898830974981]
[132.30000000000013,0.65934315899999918,1292.3125916399983]
[133.87500000000011,0.64802417343749907,1270.1273799374983]
[135.4500000000001,0.63680318774999933,1248.1342479899986]
[137.02500000000009,0.6256802019374994,1226.3331957974988]
[138.60000000000008,0.6146552159999995,1204.7242233599991]
[140.17500000000007,0.60372822993749953,1183.3073306774991]
[141.75000000000006,0.59289924374999969,1162.0825177499994]
[143.32500000000005,0.58216825743749967,1141.0497845774994]
[144.90000000000003,0.57153527099999979,1120.2091311599995]
[146.47500000000002,0.56100028443749983,1099.5605574974998]
[148.05000000000001,0.5505632977499999,1079.1040635899999]
[149.625,0.54022431093750001,1058.8396494374999]
[151.19999999999999,0.52998332400000003,1038.7673150400001]
[152.77499999999998,0.5198403369375002,1018.8870603975004]
[154.34999999999997,0.50979534975000018,999.19888551000042]
[155.92499999999995,0.4998483624375003,979.70279037750061]
[157.49999999999994,0.48999937500000035,960.39877500000068]
[159.07499999999993,0.48024838743750042,941.28683937750088]
[160.64999999999992,0.47059539975000048,922.36698351000098]
[162.22499999999991,0.46104041193750056,903.63920739750108]
[163.7999999999999,0.45158342400000062,885.10351104000119]
[165.37499999999989,0.44222443593750066,866.75989443750132]
[166.94999999999987,0.43296344775000073,848.60835759000145]
[168.52499999999986,0.42380045943750083,830.64890049750159]
[170.09999999999985,0.4147354710000008,812.88152316000162]
[171.67499999999984,0.40576848243750091,795.30622557750178]
[173.24999999999983,0.39689949375000094,777.92300775000183]
[174.82499999999982,0.38812850493750101,760.731869677502]
[176.39999999999981,0.37945551600000105,743.73281136000207]
[177.9749999999998,0.37088052693750118,726.92583279750227]
[179.54999999999978,0.36240353775000117,710.31093399000224]
[181.12499999999977,0.35402454843750125,693.88811493750245]
[182.69999999999976,0.34574355900000125,677.65737564000244]
[184.27499999999975,0.33756056943750123,661.61871609750244]
[185.84999999999974,0.32947557975000136,645.77213631000268]
[187.42499999999973,0.3214885899375014,630.1176362775027]
[188.99999999999972,0.31359960000000137,614.65521600000272]
[190.5749999999997,0.30580860993750147,599.38487547750287]
[192.14999999999969,0.2981156197500015,584.30661471000292]
[193.72499999999968,0.29052062943750151,569.42043369750297]
[195.29999999999967,0.28302363900000155,554.72633244000303]
[196.87499999999966,0.27562464843750156,540.22431093750311]
[198.44999999999965,0.26832365775000161,525.91436919000319]
[200.02499999999964,0.26112066693750169,511.79650719750327]
[201.59999999999962,0.25401567600000169,497.87072496000332]
[203.17499999999961,0.24700868493750169,484.13702247750331]
[204.7499999999996,0.24009969375000173,470.59539975000337]
[206.32499999999959,0.23328870243750174,457.24585677750343]
[207.89999999999958,0.22657571100000179,444.08839356000351]
[209.47499999999957,0.21996071943750181,431.12301009750354]
[211.04999999999956,0.21344372775000181,418.34970639000358]
[212.62499999999955,0.20702473593750184,405.76848243750362]
[214.19999999999953,0.20070374400000185,393.37933824000362]
[215.77499999999952,0.19448075193750189,381.18227379750368]
[217.34999999999951,0.18835575975000188,369.1772891100037]
[218.9249999999995,0.1823287674375019,357.36438417750372]
[220.49999999999949,0.17639977500000192,345.74355900000376]
[222.07499999999948,0.1705687824375019,334.31481357750374]
[223.64999999999947,0.16483578975000193,323.07814791000379]
[225.22499999999945,0.15920079693750194,312.0335619975038]
[226.79999999999944,0.15366380400000193,301.18105584000381]
[228.37499999999943,0.14822481093750195,290.52062943750383]
[229.94999999999942,0.14288381775000195,280.0522827900038]
[231.52499999999941,0.13764082443750195,269.77601589750384]
[233.0999999999994,0.13249583100000195,259.69182876000383]
[234.67499999999939,0.12744883743750193,249.7997213775038]
[236.24999999999937,0.12249984375000195,240.09969375000381]
[237.82499999999936,0.11764884993750194,230.5917458775038]
[239.39999999999935,0.11289585600000193,221.27587776000379]
[240.97499999999934,0.10824086193750193,212.15208939750377]
[242.54999999999933,0.10368386775000192,203.22038079000376]
[244.12499999999932,9.9224873437501901E-2,194.48075193750373]
[245.69999999999931,9.4863879000001899E-2,185.93320284000373]
[247.2749999999993,9.0600884437501875E-2,177.57773349750369]
[248.84999999999928,8.6435889750001882E-2,169.41434391000368]
[250.42499999999927,8.2368894937501852E-2,161.44303407750363]
[251.99999999999926,7.839990000000184E-2,153.66380400000361]
[253.57499999999925,7.4528904937501819E-2,146.07665367750357]
[255.14999999999924,7.0755909750001789E-2,138.68158311000352]
[256.72499999999923,6.708091443750179E-2,131.4785922975035]
[258.29999999999922,6.3503919000001754E-2,124.46768124000344]
[259.8749999999992,6.0024923437501737E-2,117.6488499375034]
[261.44999999999919,5.664392775000171E-2,111.02209839000335]
[263.02499999999918,5.3360931937501681E-2,104.5874265975033]
[264.59999999999917,5.0175936000001649E-2,98.344834560003235]
[266.17499999999916,4.7088939937501621E-2,92.294322277503184]
[267.74999999999915,4.4099943750001591E-2,86.435889750003113]
[269.32499999999914,4.1208947437501559E-2,80.769536977503051]
[270.89999999999912,3.841595100000153E-2,75.295263960002998]
[272.47499999999911,3.5720954437501493E-2,70.013070697502926]
[274.0499999999991,3.3123957750001452E-2,64.922957190002847]
[275.62499999999909,3.0624960937501413E-2,60.024923437502771]
[277.19999999999908,2.8223964000001375E-2,55.318969440002697]
[278.77499999999907,2.592096693750133E-2,50.805095197502609]
[280.34999999999906,2.371596975000129E-2,46.483300710002531]
[281.92499999999905,2.1608972437501248E-2,42.353585977502448]
[283.49999999999903,1.9599975000001203E-2,38.415951000002359]
[285.07499999999902,1.7688977437501155E-2,34.670395777502264]
[286.64999999999901,1.5875979750001108E-2,31.116920310002172]
[288.224999999999,1.4160981937501057E-2,27.755524597502074]
[289.79999999999899,1.2543984000001007E-2,24.586208640001974]
[291.37499999999898,1.1024985937500955E-2,21.608972437501873]
[292.94999999999897,9.6039877500009013E-3,18.823815990001766]
[294.52499999999895,8.2809894375008471E-3,16.23073929750166]
[296.09999999999894,7.0559910000007886E-3,13.829742360001546]
[297.67499999999893,5.9289924375007319E-3,11.620825177501434]
[299.24999999999892,4.8999937500006727E-3,9.603987750001318]
[300.82499999999891,3.9689949375006119E-3,7.7792300775011984]
[302.3999999999989,3.1359960000005489E-3,6.1465521600010762]
[303.97499999999889,2.4009969375004855E-3,4.7059539975009512]
[305.54999999999887,1.7639977500004203E-3,3.4574355900008236]
[307.12499999999886,1.2249984375003536E-3,2.4009969375006932]
[308.69999999999885,7.8399900000028565E-4,1.5366380400005599]
[310.27499999999884,4.4099943750021647E-4,0.86435889750042427]
[311.84999999999883,1.9599975000014571E-4,0.38415951000028559]
[313.42499999999882,4.8999937500073574E-5,9.60398775001442E-2]
[314.99999999999881,2.8147082164104214E-29,5.5168281041644262E-26]