{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["HRR","Options","Output"],"not_rendered":{"charts":1,"images":2,"macros":1,"external_links":0,"defined_names":14,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"HRR","index":0,"n_rows":22,"n_cols":4,"rows_kept":22,"cut":false,"hidden":false,"merged":[[3,1,3,3],[17,1,17,3]]}
[]
["Wood Crib HRR Ref: The SFPE Handbook of Fire Protection Engineering, Third Edition"]
[]
[null,"Input Data"]
[null,"D =",0.04,"m"]
[null,"S =",0.06,"m"]
[null,"hC =",0.56000000000000005,"m"]
[null,"n =",5,"sticks/row"]
[null,"AV =",4,"m^2"]
[null,"hV =",2,"m"]
[null,"m0 =",20.7,"kg"]
[null,"HoC =",17900,"kJ/kg"]
[null,"Ignition =","Center","Select"]
[]
[]
[]
[]
[null,"Calculated Data"]
[null,"vP =",1.517702627607336E-5]
[null,"Surface Control HRR =",562.35435460734618,"kJ/s"]
[null,"Porosity Control HRR =",436.69607142857137,"kJ/s"]
[null,"Vent Control HRR =",12150.922927909633,"kJ/s"]

{"sheet":"Options","index":1,"n_rows":3,"n_cols":2,"rows_kept":3,"cut":false,"hidden":false,"merged":[]}
["Ignition Options:"]
[null,"Instantaneous"]
[null,"Center"]

{"sheet":"Output","index":2,"n_rows":422,"n_cols":4,"rows_kept":422,"cut":false,"hidden":false,"merged":[]}
["Output Data"]
[]
["t(s)","m_dot","HRR","Integral"]
[0,0,0,0]
[3.2944530167167985,8.66078753564679E-5,1.5502809688807755,2.5536639073439562]
[6.5889060334335969,3.464315014258716E-4,6.201123875523102,15.321983444063736]
[9.8833590501503963,7.7947087820821133E-4,13.952528719926983,48.519614239535173]
[13.177812066867194,1.3857260057034864E-3,24.804495502092408,112.36121192313405]
[16.472265083583991,2.1651968839116976E-3,38.757024222019389,217.06143212423621]
[19.766718100300789,3.117883512832844E-3,55.810114879707911,372.83493047221748]
[23.061171117017587,4.2437858924669267E-3,75.963767475157994,589.89636259645363]
[26.355624133734384,5.5429040228139447E-3,99.217982008369617,878.4603841263206]
[29.650077150451182,7.0152379038738982E-3,125.57275847934278,1248.7416506911941]
[32.944530167167983,8.6607875356467905E-3,155.02809688807756,1710.9548179204503]
[36.238983183884784,1.0479552918132616E-2,187.58399723457384,2275.3145414434648]
[39.533436200601585,1.2471534051331381E-2,223.24045951883173,2952.0354768896141]
[42.827889217318386,1.463673093524308E-2,261.99748374085112,3751.3322798882732]
[46.122342234035187,1.6975143569867717E-2,303.85506990063215,4683.4196060688182]
[49.416795250751989,1.9486771955205286E-2,348.81321799817465,5758.5121110606251]
[52.71124826746879,2.2171616091255796E-2,396.87192803347875,6986.8244504930699]
[56.005701284185591,2.4396428571428569E-2,436.69607142857137,8359.8997557262392]
[59.300154300902392,2.4396428571428569E-2,436.69607142857137,9798.5744456324719]
[62.594607317619193,2.4396428571428569E-2,436.69607142857137,11237.249135538705]
[65.889060334335994,2.4396428571428569E-2,436.69607142857137,12675.923825444937]
[69.183513351052795,2.4396428571428569E-2,436.69607142857137,14114.59851535117]
[72.477966367769596,2.4396428571428569E-2,436.69607142857137,15553.273205257403]
[75.772419384486398,2.4396428571428569E-2,436.69607142857137,16991.947895163634]
[79.066872401203199,2.4396428571428569E-2,436.69607142857137,18430.622585069865]
[82.36132541792,2.4396428571428569E-2,436.69607142857137,19869.297274976096]
[85.655778434636801,2.4396428571428569E-2,436.69607142857137,21307.971964882327]
[88.950231451353602,2.4396428571428569E-2,436.69607142857137,22746.646654788557]
[92.244684468070403,2.4396428571428569E-2,436.69607142857137,24185.321344694788]
[95.539137484787204,2.4396428571428569E-2,436.69607142857137,25623.996034601019]
[98.833590501504005,2.4396428571428569E-2,436.69607142857137,27062.67072450725]
[102.12804351822081,2.4396428571428569E-2,436.69607142857137,28501.345414413481]
[105.42249653493761,2.4396428571428569E-2,436.69607142857137,29940.020104319712]
[108.71694955165441,2.4396428571428569E-2,436.69607142857137,31378.694794225943]
[112.01140256837121,2.4396428571428569E-2,436.69607142857137,32817.369484132178]
[115.30585558508801,2.4396428571428569E-2,436.69607142857137,34256.044174038412]
[118.60030860180481,2.4396428571428569E-2,436.69607142857137,35694.718863944647]
[121.89476161852161,2.4396428571428569E-2,436.69607142857137,37133.393553850881]
[125.18921463523841,2.4396428571428569E-2,436.69607142857137,38572.068243757116]
[128.48366765195522,2.4396428571428569E-2,436.69607142857137,40010.74293366335]
[131.77812066867202,2.4396428571428569E-2,436.69607142857137,41449.417623569585]
[135.07257368538882,2.4396428571428569E-2,436.69607142857137,42888.09231347582]
[138.36702670210562,2.4396428571428569E-2,436.69607142857137,44326.767003382054]
[141.66147971882242,2.4396428571428569E-2,436.69607142857137,45765.441693288289]
[144.95593273553922,2.4396428571428569E-2,436.69607142857137,47204.116383194523]
[148.25038575225602,2.4396428571428569E-2,436.69607142857137,48642.791073100758]
[151.54483876897282,2.4396428571428569E-2,436.69607142857137,50081.465763006992]
[154.83929178568962,2.4396428571428569E-2,436.69607142857137,51520.140452913227]
[158.13374480240643,2.4396428571428569E-2,436.69607142857137,52958.815142819461]
[161.42819781912323,2.4396428571428569E-2,436.69607142857137,54397.489832725696]
[164.72265083584003,2.4396428571428569E-2,436.69607142857137,55836.164522631931]
[168.01710385255683,2.4396428571428569E-2,436.69607142857137,57274.839212538165]
[171.31155686927363,2.4396428571428569E-2,436.69607142857137,58713.5139024444]
[174.60600988599043,2.4396428571428569E-2,436.69607142857137,60152.188592350634]
[177.90046290270723,2.4396428571428569E-2,436.69607142857137,61590.863282256869]
[181.19491591942403,2.4396428571428569E-2,436.69607142857137,63029.537972163103]
[184.48936893614083,2.4396428571428569E-2,436.69607142857137,64468.212662069338]
[187.78382195285764,2.4396428571428569E-2,436.69607142857137,65906.887351975573]
[191.07827496957444,2.4396428571428569E-2,436.69607142857137,67345.5620418818]
[194.37272798629124,2.4396428571428569E-2,436.69607142857137,68784.236731788027]
[197.66718100300804,2.4396428571428569E-2,436.69607142857137,70222.911421694254]
[200.96163401972484,2.4396428571428569E-2,436.69607142857137,71661.586111600482]
[204.25608703644164,2.4396428571428569E-2,436.69607142857137,73100.260801506709]
[207.55054005315844,2.4396428571428569E-2,436.69607142857137,74538.935491412936]
[210.84499306987524,2.4396428571428569E-2,436.69607142857137,75977.610181319164]
[214.13944608659205,2.4396428571428569E-2,436.69607142857137,77416.284871225391]
[217.43389910330885,2.4396428571428569E-2,436.69607142857137,78854.959561131618]
[220.72835212002565,2.4396428571428569E-2,436.69607142857137,80293.634251037845]
[224.02280513674245,2.4396428571428569E-2,436.69607142857137,81732.308940944073]
[227.31725815345925,2.4396428571428569E-2,436.69607142857137,83170.9836308503]
[230.61171117017605,2.4396428571428569E-2,436.69607142857137,84609.658320756527]
[233.90616418689285,2.4396428571428569E-2,436.69607142857137,86048.333010662755]
[237.20061720360965,2.4396428571428569E-2,436.69607142857137,87487.007700568982]
[240.49507022032645,2.4396428571428569E-2,436.69607142857137,88925.682390475209]
[243.78952323704326,2.4396428571428569E-2,436.69607142857137,90364.357080381436]
[247.08397625376006,2.4396428571428569E-2,436.69607142857137,91803.031770287664]
[250.37842927047686,2.4396428571428569E-2,436.69607142857137,93241.706460193891]
[253.67288228719366,2.4396428571428569E-2,436.69607142857137,94680.381150100118]
[256.96733530391043,2.4396428571428569E-2,436.69607142857137,96119.055840006346]
[260.2617883206272,2.4396428571428569E-2,436.69607142857137,97557.730529912573]
[263.55624133734398,2.4396428571428569E-2,436.69607142857137,98996.4052198188]
[266.85069435406075,2.4396428571428569E-2,436.69607142857137,100435.07990972503]
[270.14514737077752,2.4396428571428569E-2,436.69607142857137,101873.75459963125]
[273.43960038749429,2.4396428571428569E-2,436.69607142857137,103312.42928953748]
[276.73405340421107,2.4396428571428569E-2,436.69607142857137,104751.10397944371]
[280.02850642092784,2.4396428571428569E-2,436.69607142857137,106189.77866934994]
[283.32295943764461,2.4396428571428569E-2,436.69607142857137,107628.45335925616]
[286.61741245436139,2.4396428571428569E-2,436.69607142857137,109067.12804916239]
[289.91186547107816,2.4396428571428569E-2,436.69607142857137,110505.80273906862]
[293.20631848779493,2.4396428571428569E-2,436.69607142857137,111944.47742897485]
[296.5007715045117,2.4396428571428569E-2,436.69607142857137,113383.15211888107]
[299.79522452122848,2.4396428571428569E-2,436.69607142857137,114821.8268087873]
[303.08967753794525,2.4396428571428569E-2,436.69607142857137,116260.50149869353]
[306.38413055466202,2.4396428571428569E-2,436.69607142857137,117699.17618859975]
[309.67858357137879,2.4396428571428569E-2,436.69607142857137,119137.85087850598]
[312.97303658809557,2.4396428571428569E-2,436.69607142857137,120576.52556841221]
[316.26748960481234,2.4396428571428569E-2,436.69607142857137,122015.20025831844]
[319.56194262152911,2.4396428571428569E-2,436.69607142857137,123453.87494822466]
[322.85639563824589,2.4396428571428569E-2,436.69607142857137,124892.54963813089]
[326.15084865496266,2.4396428571428569E-2,436.69607142857137,126331.22432803712]
[329.44530167167943,2.4396428571428569E-2,436.69607142857137,127769.89901794335]
[332.7397546883962,2.4396428571428569E-2,436.69607142857137,129208.57370784957]
[336.03420770511298,2.4396428571428569E-2,436.69607142857137,130647.2483977558]
[339.32866072182975,2.4396428571428569E-2,436.69607142857137,132085.92308766203]
[342.62311373854652,2.4396428571428569E-2,436.69607142857137,133524.59777756824]
[345.91756675526329,2.4396428571428569E-2,436.69607142857137,134963.27246747445]
[349.21201977198007,2.4396428571428569E-2,436.69607142857137,136401.94715738067]
[352.50647278869684,2.4396428571428569E-2,436.69607142857137,137840.62184728688]
[355.80092580541361,2.4396428571428569E-2,436.69607142857137,139279.29653719309]
[359.09537882213039,2.4396428571428569E-2,436.69607142857137,140717.9712270993]
[362.38983183884716,2.4396428571428569E-2,436.69607142857137,142156.64591700552]
[365.68428485556393,2.4396428571428569E-2,436.69607142857137,143595.32060691173]
[368.9787378722807,2.4396428571428569E-2,436.69607142857137,145033.99529681794]
[372.27319088899748,2.4396428571428569E-2,436.69607142857137,146472.66998672416]
[375.56764390571425,2.4396428571428569E-2,436.69607142857137,147911.34467663037]
[378.86209692243102,2.4351522589349642E-2,435.89225434935861,149348.69529773583]
[382.15654993914779,2.4272781756063806E-2,434.4827934335421,150782.40014865753]
[385.45100295586457,2.4193985353671062E-2,433.072337830712,152211.45995833835]
[388.74545597258134,2.4115188026621444E-2,431.66186567652386,153635.87306103966]
[392.03990898929811,2.4036389858120469E-2,430.25137846035636,155055.6394046871]
[395.33436200601489,2.3957590842760307E-2,428.84087608540949,156470.75893950026]
[398.62881502273166,2.3878790974933718E-2,427.43035845131357,157881.23161537392]
[401.92326803944843,2.3799990248977287E-2,426.01982545669341,159287.05738187055]
[405.2177210561652,2.372118865917091E-2,424.60927699915931,160688.23618821692]
[408.51217407288198,2.364238619973703E-2,423.19871297529284,162084.76798330087]
[411.80662708959875,2.3563582864839876E-2,421.78813328063382,163476.65271566779]
[415.10108010631552,2.348477864858467E-2,420.37753780966557,164863.89033351716]
[418.39553312303229,2.3405973545016827E-2,418.96692645580123,166246.48078469912]
[421.68998613974907,2.3327167548121142E-2,417.55629911136845,167624.42401671081]
[424.98443915646584,2.3248360651820971E-2,416.14565566759541,168997.71997669293]
[428.27889217318261,2.3169552849977387E-2,414.7349960145952,170366.36861142592]
[431.57334518989938,2.3090744136388324E-2,413.32432004135103,171730.3698673264]
[434.86779820661616,2.3011934504787706E-2,411.91362763569992,173089.72369044332]
[438.16225122333293,2.2933123948844562E-2,410.50291868431765,174444.43002645421]
[441.4567042400497,2.285431246216213E-2,409.09219307270212,175794.48882066133]
[444.75115725676648,2.2775500038276948E-2,407.68145068515736,177139.90001798773]
[448.04561027348325,2.2696686670657901E-2,406.27069140477641,178480.66356297335]
[451.34006329020002,2.2617872352705289E-2,404.85991511342468,179816.77939977095]
[454.63451630691679,2.2539057077749867E-2,403.44912169172261,181148.24747214201]
[457.92896932363357,2.2460240839051848E-2,402.03831101902807,182475.0677234527]
[461.22342234035034,2.2381423629799925E-2,400.62748297341864,183797.24009666959]
[464.51787535706711,2.2302605443110222E-2,399.21663743167295,185114.76453435546]
[467.81232837378388,2.2223786272025287E-2,397.80577426925265,186427.64097866495]
[471.10678139050066,2.2144966109513036E-2,396.39489336028333,187735.86937134023]
[474.40123440721743,2.206614494846567E-2,394.9839945775355,189039.4496537066]
[477.6956874239342,2.1987322781698581E-2,393.5730777924046,190338.38176666785]
[480.99014044065098,2.1908499601949263E-2,392.1621428748918,191632.66565070185]
[484.28459345736775,2.1829675401876147E-2,390.751189693583,192922.30124585584]
[487.57904647408452,2.1750850174057475E-2,389.34021811562883,194207.28849174178]
[490.87349949080129,2.1672023910990122E-2,387.92922800672318,195487.62732753158]
[494.16795250751807,2.1593196605088388E-2,386.51821923108213,196763.31769195216]
[497.46240552423484,2.1514368248682792E-2,385.107191651422,198034.35952328076]
[500.75685854095161,2.1435538834018837E-2,383.69614512893719,199300.75275933975]
[504.05131155766838,2.1356708353255729E-2,382.28507952327755,200562.49733749169]
[507.34576457438516,2.1277876798465122E-2,380.87399469252568,201819.59319463422]
[510.64021759110193,2.1199044161629762E-2,379.46289049317272,203072.04026719474]
[513.9346706078187,2.1120210434642208E-2,378.05176678009553,204319.83849112529]
[517.22912362453553,2.1041375609303418E-2,376.64062340653118,205562.98780189708]
[520.52357664125236,2.0962539677321403E-2,375.22946022405313,206801.48813449504]
[523.81802965796919,2.0883702630309794E-2,373.81827708254531,208035.33942341237]
[527.11248267468602,2.0804864459786413E-2,372.40707383017678,209264.54160264487]
[530.40693569140285,2.0726025157171805E-2,370.99585031337534,210489.09460568527]
[533.70138870811968,2.0647184713787726E-2,369.58460637680031,211708.9983655175]
[536.99584172483651,2.0568343120855662E-2,368.17334186331635,212924.25281461075]
[540.29029474155334,2.048950036949522E-2,366.76205661396443,214134.85788491348]
[543.58474775827017,2.0410656450722597E-2,365.35075046793452,215340.81350784749]
[546.879200774987,2.0331811355448925E-2,363.93942326253574,216542.11961430163]
[550.17365379170383,2.025296507447865E-2,362.52807483316786,217738.77613462569]
[553.46810680842066,2.0174117598507853E-2,361.11670501329058,218930.78299862397]
[556.76255982513749,2.0095268918122515E-2,359.70531363439301,220118.14013554886]
[560.05701284185432,2.0016419023796809E-2,358.2939005259629,221300.84747409431]
[563.35146585857115,1.9937567905891292E-2,356.88246551545416,222478.90494238917]
[566.64591887528798,1.9858715554651088E-2,355.47100842825449,223652.31246799044]
[569.9403718920048,1.9779861960204061E-2,354.05952908765272,224821.06997787644]
[573.23482490872163,1.9701007112558903E-2,352.64802731480438,225985.17739843976]
[576.52927792543846,1.9622151001603211E-2,351.23650292869746,227144.63465548027]
[579.82373094215529,1.9543293617101526E-2,349.82495574611733,228299.44167419785]
[583.11818395887212,1.9464434948693328E-2,348.41338558161056,229449.5983791851]
[586.41263697558895,1.9385574985890976E-2,347.00179224744846,230595.10469441992]
[589.70708999230578,1.9306713718077628E-2,345.59017555358952,231735.96054325791]
[593.00154300902261,1.9227851134505109E-2,344.17853530764143,232872.16584842475]
[596.29599602573944,1.9148987224291723E-2,342.76687131482186,234003.72053200833]
[599.59044904245627,1.9070121976420037E-2,341.35518337791865,235130.62451545085]
[602.8849020591731,1.8991255379734621E-2,339.94347129724969,236252.8777195407]
[606.17935507588993,1.8912387422939703E-2,338.53173487062071,237370.48006440437]
[609.47380809260676,1.8833518094596848E-2,337.1199738932836,238483.43146949794]
[612.76826110932359,1.8754647383122488E-2,335.70818815789255,239591.7318535987]
[616.06271412604042,1.8675775276785503E-2,334.29637745446053,240695.38113479654]
[619.35716714275725,1.8596901763704675E-2,332.88454157031367,241794.37923048506]
[622.65162015947408,1.8518026831846106E-2,331.47268029004528,242888.72605735279]
[625.94607317619091,1.8439150469020622E-2,330.06079339546915,243978.42153137398]
[629.24052619290774,1.8360272662881053E-2,328.64888066557086,245063.46556779946]
[632.53497920962457,1.8281393400919506E-2,327.23694187645913,246143.85808114716]
[635.8294322263414,1.8202512670464552E-2,325.82497680131547,247219.5989851926]
[639.12388524305823,1.8123630458678364E-2,324.4129852103427,248290.68819295915]
[642.41833825977506,1.8044746752553797E-2,323.000966870713,249357.12561670816]
[645.71279127649188,1.7965861538911367E-2,321.58892154651346,250418.9111679288]
[649.00724429320871,1.7886974804396209E-2,320.17684899869215,251476.04475732794]
[652.30169730992554,1.7808086535474964E-2,318.76474898500186,252528.52629481957]
[655.59615032664237,1.7729196718432538E-2,317.35262125994245,253576.35568951428]
[658.8906033433592,1.7650305339368868E-2,315.94046557470273,254619.53284970843]
[662.18505636007603,1.7571412384195555E-2,314.52828167710044,255658.05768287313]
[665.47950937679286,1.7492517838632458E-2,313.11606931152102,256691.93009564301]
[668.77396239350969,1.7413621688204178E-2,311.70382821885477,257721.14999380484]
[672.06841541022652,1.7334723918236494E-2,310.29155813643325,258745.71728228591]
[675.36286842694335,1.7255824513852693E-2,308.87925879796319,259765.63186514218]
[678.65732144366018,1.7176923459969812E-2,307.46692993345965,260780.89364554625]
[681.95177446037701,1.7098020741294837E-2,306.05457126917759,261791.50252577508]
[685.24622747709384,1.7019116342320739E-2,304.64218252754119,262797.4584071975]
[688.54068049381067,1.6940210247322486E-2,303.2297634270725,263798.76119026134]
[691.8351335105275,1.6861302440352922E-2,301.81731368231732,264795.41077448073]
[695.12958652724433,1.6782392905238554E-2,300.40483300377014,265787.40705842257]
[698.42403954396116,1.6703481625575264E-2,298.99232109779723,266774.74993969325]
[701.71849256067799,1.6624568584723866E-2,297.57977766655722,267757.43931492494]
[705.01294557739482,1.6545653765805617E-2,296.16720240792057,268735.47507976135]
[708.30739859411165,1.6466737151697577E-2,294.7545950153866,269708.85712884384]
[711.60185161082848,1.638781872502787E-2,293.34195517799884,270677.5853557965]
[714.89630462754531,1.6308898468170831E-2,291.92928258025785,271641.65965321165]
[718.19075764426213,1.6229976363242041E-2,290.51657690203251,272601.07991263451]
[721.48521066097896,1.6151052392093215E-2,289.10383781846855,273555.84602454782]
[724.77966367769579,1.6072126536306994E-2,287.69106499989522,274505.95787835622]
[728.07411669441262,1.5993198777191575E-2,286.2782581117292,275451.4153623702]
[731.36856971112945,1.5914269095775247E-2,284.86541681437694,276392.21836378973]
[734.66302272784628,1.5835337472800755E-2,283.45254076313353,277328.3667686875]
[737.95747574456311,1.5756403888719527E-2,282.03962960807957,278259.8604619921]
[741.25192876127994,1.5677468323685776E-2,280.62668299397541,279186.6993274705]
[744.54638177799677,1.5598530757550428E-2,279.21370056015269,280108.88324771042]
[747.8408347947136,1.5519591169854902E-2,277.80068194040274,281026.4121041022]
[751.13528781143043,1.5440649539824734E-2,276.38762676286274,281939.28577682056]
[754.42974082814726,1.5361705846363033E-2,274.97453464989832,282847.50414480543]
[757.72419384486409,1.5282760068043761E-2,273.56140521798335,283751.06708574313]
[761.01864686158092,1.5203812183104837E-2,272.14823807757659,284649.97447604639]
[764.31309987829775,1.5124862169441085E-2,270.73503283299544,285544.2261908346]
[767.60755289501458,1.504591000459695E-2,269.32178908228542,286433.82210391323]
[770.90200591173141,1.4966955665759053E-2,267.90850641708704,287318.76208775304]
[774.19645892844824,1.4887999129748542E-2,266.49518442249894,288199.04601346859]
[777.49091194516507,1.4809040373013236E-2,265.08182267693689,289074.67375079659]
[780.7853649618819,1.4730079371619532E-2,263.66842075198963,289945.64516807371]
[784.07981797859873,1.4651116101244149E-2,262.25497821227026,290811.9601322136]
[787.37427099531556,1.457215053716558E-2,260.84149461526391,291673.61850868393]
[790.66872401203238,1.4493182654255352E-2,259.42796951117077,292530.62016148242]
[793.96317702874921,1.4414212426969034E-2,258.01440244274573,293382.96495311277]
[797.25763004546604,1.4335239829336988E-2,256.60079294513207,294230.65274455975]
[800.55208306218287,1.4256264834954869E-2,255.18714054569216,295073.6833952638]
[803.8465360788997,1.4177287416973855E-2,253.773444763832,295912.05676309526]
[807.14098909561653,1.40983075480906E-2,252.35970511082175,296745.77270432771]
[810.43544211233336,1.40193252005369E-2,250.94592108961052,297574.83107361099]
[813.72989512905019,1.3940340346069075E-2,249.53209219463645,298399.23172394338]
[817.02434814576702,1.3861352955957026E-2,248.11821791163075,299218.97450664319]
[820.31880116248385,1.3782363000972978E-2,246.7042977174163,300034.05927131994]
[823.61325417920068,1.3703370451379931E-2,245.29033107970076,300844.48586584453]
[826.90770719591751,1.3624375276919707E-2,243.87631745686275,301650.25413631881]
[830.20216021263434,1.3545377446800714E-2,242.46225629773278,302451.36392704461]
[833.49661322935117,1.3466376929685296E-2,241.0481470413668,303247.81508049183]
[836.791066246068,1.3387373693676737E-2,239.63398911681358,304039.60743726592]
[840.08551926278483,1.3308367706305859E-2,238.21978194287487,304826.74083607446]
[843.37997227950166,1.3229358934517217E-2,236.80552492785819,305609.21511369303]
[846.67442529621849,1.3150347344654884E-2,235.39121746932244,306387.03010493016]
[849.96887831293532,1.3071332902447795E-2,233.97685895381554,307160.18564259156]
[853.26333132965215,1.2992315572994647E-2,232.5624487566042,307928.68155744334]
[856.55778434636898,1.2913295320748308E-2,231.1479862413947,308692.51767817448]
[859.85223736308581,1.283427210949979E-2,229.73347076004623,309451.6938313581]
[863.14669037980264,1.2755245902361665E-2,228.31890165227381,310206.20984141214]
[866.44114339651946,1.2676216661750995E-2,226.90427824534279,310956.0655305587]
[869.73559641323629,1.2597184349371704E-2,225.4895998537535,311701.26071878261]
[873.03004942995312,1.2518148926196402E-2,224.07486577891561,312441.79522378871]
[876.32450244666995,1.2439110352447606E-2,222.66007530881214,313177.66886095837]
[879.61895546338678,1.236006858757837E-2,221.24522771765282,313908.88144330442]
[882.91340848010361,1.2281023590252273E-2,219.83032226551569,314635.43278142548]
[886.20786149682044,1.2201975318322766E-2,218.41535819797753,315357.32268345851]
[889.50231451353727,1.2122923728811821E-2,217.00033474573158,316074.55095503066]
[892.7967675302541,1.204386877788788E-2,215.58525112419306,316787.11739920935]
[896.09122054697093,1.1964810420843077E-2,214.17010653309109,317495.02181645151]
[899.38567356368776,1.1885748612069667E-2,212.75490015604706,318198.26400455093]
[902.68012658040459,1.1806683305035691E-2,211.33963116013888,318896.84375858482]
[905.97457959712142,1.1727614452259774E-2,209.92429869544995,319590.76087085815]
[909.26903261383825,1.1648542005285093E-2,208.50890189460316,320280.01513084734]
[912.56348563055508,1.1569465914652424E-2,207.0934398722784,320964.60632514156]
[915.85793864727191,1.1490386129872252E-2,205.67791172471331,321644.53423738305]
[919.15239166398874,1.1411302599395901E-2,204.26231652918662,322319.79864820535]
[922.44684468070557,1.133221527058567E-2,202.8466533434835,322990.39933517011]
[925.7412976974224,1.1253124089683863E-2,201.43092120534115,323656.33607270179]
[929.03575071413923,1.1174029001780744E-2,200.01511913187531,324317.60863202077]
[932.33020373085606,1.1094929950781332E-2,198.59924611898583,324974.21678107447]
[935.62465674757289,1.1015826879370961E-2,197.18330114074021,325626.16028446628]
[938.91910976428971,1.0936719728979626E-2,195.76728314873532,326273.43890338286]
[942.21356278100654,1.0857608439744966E-2,194.3511910714349,326916.05239551869]
[945.50801579772337,1.0778492950473898E-2,192.93502381348279,327554.00051499892]
[948.8024688144402,1.0699373198602823E-2,191.51878025499053,328187.28301229974]
[952.09692183115703,1.0620249120156293E-2,190.10245925079764,328815.89963416627]
[955.39137484787386,1.0541120649704154E-2,188.68605962970437,329439.85012352804]
[958.68582786459069,1.0461987720317006E-2,187.26958019367441,330059.13421941194]
[961.98028088130752,1.0382850263519972E-2,185.8530197170075,330673.75165685243]
[965.27473389802435,1.0303708209244653E-2,184.43637694547928,331283.70216679893]
[968.56918691474118,1.0224561485779196E-2,183.01965059544762,331888.98547602043]
[971.86363993145801,1.014541001971641E-2,181.60283935292372,332489.60130700702]
[975.15809294817484,1.006625373589979E-2,180.18594187260624,333085.54937786842]
[978.45254596489167,9.9870925573673774E-3,178.76895677687605,333676.82940222893]
[981.7469989816085,9.9079264052933623E-3,177.35188265475119,334263.44108911959]
[985.04145199832533,9.8287551989272876E-3,175.93471806079845,334845.38414286607]
[988.33590501504216,9.749578855530747E-3,174.51746151400036,335422.65826297365]
[991.63035803175899,9.6703972903114666E-3,173.10011149657524,335995.26314400788]
[994.92481104847582,9.5912104163546254E-3,171.68266645274778,336563.19847547146]
[998.21926406519265,9.5120181445512621E-3,170.26512478746758,337126.46394167695]
[1001.5137170819095,9.4328203835236483E-3,168.84748486507331,337685.0592216152]
[1004.8081700986263,9.3536170395474589E-3,167.42974500789953,338238.98398881929]
[1008.1026231153431,9.2744080164705433E-3,166.01190349482272,338788.23791122372]
[1011.39707613206,9.1951932156281932E-3,164.59395855974466,339332.8206510187]
[1014.6915291487768,9.1159725357546212E-3,163.17590839000772,339872.73186449945]
[1017.9859821654936,9.0367458728905382E-3,161.75775112474062,340407.97120191006]
[1021.2804351822105,8.9575131202865709E-3,160.33948485312962,340938.53830728179]
[1024.5748881989273,8.8782741683022959E-3,158.92110761261111,341464.43281826557]
[1027.869341215644,8.7990289043006695E-3,157.502617386982,341985.65436595841]
[1031.1637942323607,8.7197772125375758E-3,156.08401210442261,342502.2025747234]
[1034.4582472490774,8.6405189740462341E-3,154.6652896354276,343014.07706200314]
[1037.7527002657941,8.561254066516177E-3,153.24644779063956,343521.27743812604]
[1041.0471532825109,8.4819823641664651E-3,151.82748431857974,344023.80330610549]
[1044.3416062992276,8.4027037376128398E-3,150.40839690326985,344521.65426143119]
[1047.6360593159443,8.3234180537284531E-3,148.98918316173931,345014.82989185263]
[1050.930512332661,8.2441251754977688E-3,147.56984064141005,345503.32977715402]
[1054.2249653493777,8.1648249618632603E-3,146.15036681735236,345987.15348892059]
[1057.5194183660944,8.0855172675644744E-3,144.7307590894041,346466.30059029534]
[1060.8138713828112,8.0062019429689799E-3,143.31101477914473,346940.77063572616]
[1064.1083243995279,7.9268788338947137E-3,141.89113112671538,347410.56317070301]
[1067.4027774162446,7.8475477814231934E-3,140.47110528747515,347875.67773148383]
[1070.6972304329613,7.7682086217030358E-3,139.05093432848435,348336.11384480965]
[1073.991683449678,7.6888611857431404E-3,137.63061522480223,348791.87102760747]
[1077.2861364663947,7.6095052991949214E-3,136.21014485558908,349242.94878668088]
[1080.5805894831115,7.5301407821228373E-3,134.78951999999879,349689.34661838721]
[1083.8750424998282,7.450767448762499E-3,133.36873733284872,350131.06400830107]
[1087.1694955165449,7.3713851072654902E-3,131.94779342005228,350568.10043086292]
[1090.4639485332616,7.291993559430064E-3,130.52668471379815,351000.45534901251]
[1093.7584015499783,7.2125926004167323E-3,129.10540754745952,351428.12821380579]
[1097.052854566695,7.1331820184477174E-3,127.68395813021414,351851.11846401455]
[1100.3473075834117,7.0537615944891762E-3,126.26233254135626,352269.42552570807]
[1103.6417606001285,6.9743311019149741E-3,124.84052672427804,352683.04881181498]
[1106.9362136168452,6.8948903061507114E-3,123.41853648009773,353091.98772166541]
[1110.2306666335619,6.8154389642965992E-3,121.99635746090912,353496.24164051097]
[1113.5251196502786,6.7359768247276398E-3,120.57398516262475,353895.809939022]
[1116.8195726669953,6.6565036266694744E-3,119.15141491738359,354290.6919727606]
[1120.114025683712,6.5770190997480682E-3,117.72864188549042,354680.88708162773]
[1123.4084787004288,6.4975229635112833E-3,116.30566104685197,355066.39458928304]
[1126.7029317171455,6.4180149269202061E-3,114.88246719187168,355447.21380253561]
[1129.9973847338622,6.3384946878078906E-3,113.45905491176124,355823.34401070361]
[1133.2918377505789,6.2589619323029835E-3,112.03541858822341,356194.7844849411]
[1136.5862907672956,6.1794163342154471E-3,110.61155238245651,356561.5344775297]
[1139.8807437840123,6.0998575543813535E-3,109.18745022342623,356923.59322113282]
[1143.1751968007291,6.0202852399634174E-3,107.76310579534517,357280.95992801001]
[1146.4696498174458,5.9406990237036326E-3,106.33851252429503,357633.63378918852]
[1149.7641028341625,5.8610985231240045E-3,104.91366356391968,357981.61397358944]
[1153.0585558508792,5.7814833396709776E-3,103.4885517801105,358324.89962710475]
[1156.3530088675959,5.7018530577987491E-3,102.06316973459761,358663.48987162247]
[1159.6474618843126,5.6222072439860984E-3,100.63750966735117,358997.38380399562]
[1162.9419149010293,5.5425454456808935E-3,99.211563477687989,359326.58049495099]
[1166.2363679177461,5.4628671901657431E-3,97.785322703966798,359651.07898793346]
[1169.5308209344628,5.3831719833376283E-3,96.358778501743544,359970.87829788093]
[1172.8252739511795,5.3034593083935259E-3,94.931921620244111,360285.97740992432]
[1176.1197269678962,5.2237286244132021E-3,93.504742376996319,360596.37527800718]
[1179.4141799846129,5.1439793648293212E-3,92.077230630444845,360902.0708234185]
[1182.7086330013296,5.0642109357739258E-3,90.649375750353272,361203.0629332313]
[1186.0030860180464,4.9844227142890937E-3,89.221166585774782,361499.35045864014]
[1189.2975390347631,4.9046140463880911E-3,87.792591430346832,361790.93221318844]
[1192.5919920514798,4.824784244951765E-3,86.363637984636597,362077.80697087653]
[1195.8864450681965,4.7449325874430372E-3,84.934293315230363,362359.97346414061]
[1199.1808980849132,4.6650583134202313E-3,83.504543810222145,362637.43038169073]
[1202.4753511016299,4.5851606218275656E-3,82.07437513071342,362910.17636619555]
[1205.7698041183467,4.5052386680383277E-3,80.643772157886062,363178.21001180029]
[1209.0642571350634,4.4252915606230849E-3,79.212718935153219,363441.5298614619]
[1212.3587101517801,4.3453183578115598E-3,77.781198604826926,363700.13440408476]
[1215.6531631684968,4.2653180636125681E-3,76.349193338664975,363954.02207143774]
[1218.9476161852135,4.1852896235514614E-3,74.916684261571163,364203.19123483094]
[1222.2420692019302,4.105231919978785E-3,73.483651367620254,364447.64020152861]
[1225.536522218647,4.0251437668971726E-3,72.050073427459395,364687.36721087119]
[1228.8309752353637,3.945023904245685E-3,70.615927885997763,364922.3704300762]
[1232.1254282520804,3.8648709915716411E-3,69.181190749132369,365152.64794968412]
[1235.4198812687971,3.7846836010091709E-3,67.745836458064161,365378.19777861051]
[1238.7143342855138,3.7044602094710622E-3,66.309837749532008,365599.01783876109]
[1242.0087873022305,3.6241991899452998E-3,64.87316550002086,365815.10595915985]
[1245.3032403189472,3.5438988017698339E-3,63.435788551680027,366026.45986953354]
[1248.597693335664,3.463557179737663E-3,61.997673517304172,366233.07719328871]
[1251.8921463523807,3.3831723218586606E-3,60.558784561270024,366434.95543980628]
[1255.1865993690974,3.3027420755736654E-3,59.11908315276861,366632.09199596866]
[1258.4810523858141,3.2222641221789933E-3,57.678527787003979,366824.48411682155]
[1261.7755054025308,3.1417359591741148E-3,56.237073669216656,367012.12891525583]
[1265.0699584192475,3.0611548801897977E-3,54.794672355397381,367195.02335057687]
[1268.3644114359643,2.9805179520859624E-3,53.351271342338727,367373.16421580722]
[1271.658864452681,2.8998219887244893E-3,51.906813598168362,367546.54812354024]
[1274.9533174693977,2.8190635208179501E-3,50.461237022641306,367715.17149013182]
[1278.2477704861144,2.7382387611249613E-3,49.014473824136807,367879.03051797644]
[1281.5422235028311,2.6573435640991198E-3,47.566449797374247,368038.1211755675]
[1284.8366765195478,2.5763733788911475E-3,46.117083482151543,368192.4391749822]
[1288.1311295362646,2.495323194339481E-3,44.666285178676709,368341.97994635836]
[1291.4255825529813,2.4141874742447606E-3,43.213955788981217,368486.7386088412]
[1294.720035569698,2.3329600807832115E-3,41.759985446019485,368626.70993736316]
[1298.0144885864147,2.2516341833380459E-3,40.304251881751021,368761.88832447765]
[1301.3089416031314,2.170202149267626E-3,38.846618471890508,368892.26773628383]
[1304.6033946198481,2.0886554121149529E-3,37.386931876857659,369017.84166124457]
[1307.8978476365648,2.0069843113951205E-3,35.925019173972657,369138.60305039497]
[1311.1923006532816,1.9251778962301777E-3,34.460684342520182,369254.5442470368]
[1314.4867536699983,1.8432236825187507E-3,32.993703917085639,369365.65690348315]
[1317.781206686715,1.7611073497062104E-3,31.523821559741165,369471.93188170227]
[1321.0756597034317,1.6788123580624944E-3,30.050741209318648,369573.35913373606]
[1324.3701127201484,1.5963194599007255E-3,28.574118332222987,369669.92755642167]
[1327.6645657368651,1.5136060671367864E-3,27.093548601748477,369761.62481305376]
[1330.9590187535819,1.4306454209617445E-3,25.608553035215227,369848.43711191637]
[1334.2534717702986,1.3474054837512418E-3,24.118558159147231,369930.3489276598]
[1337.5479247870153,1.2638474327352311E-3,22.622869045960638,370007.34264559054]
[1340.842377803732,1.1799235687637863E-3,21.120631880871777,370079.39809988561]
[1344.1368308204487,1.0955743419271264E-3,19.610780720495562,370146.49196244549]
[1347.4312838371654,1.0107240002857987E-3,18.091959605115797,370208.59691574756]
[1350.7257368538822,9.2527400963378034E-4,16.562404772444669,370265.6805033806]
[1354.0201898705989,8.3909269949879596E-4,15.019759321028447,370317.70348126668]
[1357.3146428873156,7.5199816279237477E-4,13.460767113983508,370364.61735938245]
[1360.6090959040323,6.6372825226197285E-4,11.880735715489314,370406.36055460479]
[1363.903548920749,5.7388367059056612E-4,10.272517703571134,370442.85198088305]
[1367.1980019374657,4.8180810701896977E-4,8.6243651156395593,370473.97942718817]
[1370.4924549541824,3.8629502575711854E-4,6.9146809610524222,370499.5757558003]
[1373.7869079708992,2.8467887598553331E-4,5.0957518801410462,370519.35965915315]
[1377.0813609876159,1.6835387358721319E-4,3.0135343372111163,370532.71749037423]